## FWT
Project:
Unit Tag #:
Customer:
File #:
[7 empty] | Date: | 2020-03-17
Leaders in Air Flow Management
FANWALL TECHNOLOGY®
CFM (Total) | SP (in w.c.) | Operating BHP (Total) |  | Operating BHP (Per Fan) | Wheel Size " | Wheel Width % |  | Speed
1050 | 1.2149 | 0.27117 |  | 0.27117 | 12 | 100 |  | 1800
Peak SP (in w.c.) |  |  |  | Altitude Ft | Temperature oF | Density |  | Standard Air BHP | Model
1.499 | 100 | W H | 100 | 0 | 70 | 0.074996 |  | 0.27118 | 12.25
% of Peak Static Efficiency |  | % of Peak Static Pressure |  | Motor Name Plate RPM | Operating Hz | Motor HP Recommended |  | Max RPM for Class | Wheel Class
100.0745 |  | 81.0452 |  | 1760 | 61.3636 | 0.5 |  | 3525 | I
Nortek Air Solutions LLC Certifies that the Huntair PL 10 model shown herein is licensed
to bear the AMCA Seal.
The ratings shown are based on tests and procedures performed in accordance with AMCA
Publication 211 and comply with the requirements of the AMCA Certified Ratings Program.
Power rating (BHP) does not include transmission losses.
AMCA Licensed for Air Performance Without Appurtenances and Accessories
Performance certified for installation Type A: Free Inlet, Free Outlet.
NAS FAN SELECTOR PROGRAM V2.0
2017-10-01 |  |  | Nortek Air Solutions, 4841 N Sewell, Oklahoma City, OK 73118 Phone: (405) 525-6546
N
1
Generate PDF

## 12 Data
12" Wheel Test | Date: 2/19/10 | Test #AMCA |  |  | Diameter In | Width % | Blade | Angle
| Test RPM | 1800 |  |  | 12.25 | 100 | 14.25 | 48 | HUNTAIR PL 10 | 1800 | RPM
| CFM | SP | Power (BHP)
1 | 0 | 1.5309 | 0.051008 | [6 empty] | Motor HP
2 | 3 | 1.5317 | 0.052104 | [6 empty] | 0.001 | 0.5
3 | 6 | 1.5322 | 0.053169 |  | Speed (RPM) | 1800 |  |  |  | 0.5 | 0.5
4 | 9 | 1.5325 | 0.054206 |  | Diameter | 12.25 |  |  |  | 0.51 | 0.75
5 | 12 | 1.5326 | 0.055215 |  | Width Factor* | 2 |  |  |  | 0.75 | 0.75
6 | 15 | 1.5324 | 0.056197 |  | *Note: Width Factor of 1 is 50% |  |  |  |  | 0.751 | 1
7 | 18 | 1.5321 | 0.057153 | [6 empty] | 1 | 1
8 | 21 | 1.5315 | 0.058085 | [6 empty] | 1.01 | 1.5
9 | 24 | 1.5308 | 0.058993 |  | Nominal | Actual |  |  |  | 1.5 | 1.5
10 | 27 | 1.5299 | 0.059878 | [6 empty] | 1.51 | 2
11 | 30 | 1.5288 | 0.060741 |  | 12 | 12.25 |  |  |  | 2 | 2
12 | 33 | 1.5276 | 0.061583 |  | 13 | N/A |  |  |  | 2.01 | 3
13 | 36 | 1.5263 | 0.062406 |  | 14 | 13.5 |  |  |  | 3 | 3
14 | 39 | 1.5248 | 0.063209 |  | 16 | 16.5 |  |  |  | 3.01 | 5
15 | 42 | 1.5232 | 0.063994 |  | 18 | 18.25 |  |  |  | 5 | 5
16 | 45 | 1.5215 | 0.064761 |  | 20 | 20 |  |  |  | 5.01 | 7.5
17 | 48 | 1.5197 | 0.065512 |  | 22 | 22.25 |  |  |  | 7.5 | 7.5
18 | 51 | 1.5178 | 0.066247 | [6 empty] | 7.51 | 10
19 | 54 | 1.5158 | 0.066967 | [6 empty] | 10 | 10
20 | 57 | 1.5138 | 0.067672 | [6 empty] | 10.01 | 15
21 | 60 | 1.5117 | 0.068364 | [6 empty] | 15 | 15
22 | 63 | 1.5095 | 0.069043 | [6 empty] | 15.01 | 20
23 | 66 | 1.5073 | 0.06971 | [6 empty] | 20 | 20
24 | 69 | 1.505 | 0.070365 | [6 empty] | 20.01 | 25
25 | 72 | 1.5027 | 0.07101 | [6 empty] | 25 | 25
26 | 75 | 1.5004 | 0.071644 | [6 empty] | 25.01 | 30
27 | 78 | 1.498 | 0.072268 | [6 empty] | 30 | 30
28 | 81 | 1.4957 | 0.072883 | [6 empty] | 30.01 | 40
29 | 84 | 1.4933 | 0.07349 | [6 empty] | 40 | 40
30 | 87 | 1.4909 | 0.074089 | [6 empty] | 40.01 | 50
31 | 90 | 1.4885 | 0.07468 | [6 empty] | 50 | 50
32 | 93 | 1.4861 | 0.075264 | [6 empty] | 50.01 | 60
33 | 96 | 1.4837 | 0.075842 | [6 empty] | 60 | 60
34 | 99 | 1.4813 | 0.076414 | [6 empty] | 60.01 | 75
35 | 102 | 1.479 | 0.07698 | [6 empty] | 75 | 75
36 | 105 | 1.4766 | 0.077542 | [6 empty] | 75.01 | 100
37 | 108 | 1.4743 | 0.078098 | [6 empty] | 100 | 100
38 | 111 | 1.4721 | 0.078651 | [6 empty] | 100.01 | 125
39 | 114 | 1.4698 | 0.079199 | [6 empty] | 125 | 125
40 | 117 | 1.4676 | 0.079744 | [6 empty] | 125.01 | 150
41 | 120 | 1.4654 | 0.080287 | [6 empty] | 150 | 150
42 | 123 | 1.4633 | 0.080826 | [6 empty] | 150.01 | 200
43 | 126 | 1.4612 | 0.081363 | [6 empty] | 200 | 200
44 | 129 | 1.4591 | 0.081898
45 | 132 | 1.4571 | 0.082431 |  | Equations Derived from AMCA Test Data Test No. 26668A-4
46 | 135 | 1.4551 | 0.082963 |  | Performance Equation
47 | 138 | 1.4532 | 0.083493 |  | y = -0.000000000000000078243963465641x6 + 0.000000000000210750632830571000x5 - 0.000000000209682892628504000000x4 + 0.000000089101177903287000000000x3 - 0.000015159779345408400000000000x2 + 0.000310944148168346000000000000x + 1.530893080361320000000000000000
48 | 141 | 1.4514 | 0.084023 |  | Power Equation
49 | 144 | 1.4496 | 0.084552 |  | y = -0.000000000000000003041661614361x6 + 0.000000000000010778645077994800x5 - 0.000000000013493849605945300000x4 + 0.000000007143826207889680000000x3 - 0.000001734259892721690000000000x2 + 0.000370385975202225000000000000x + 0.051008048976081400000000000000
50 | 147 | 1.4478 | 0.08508
51 | 150 | 1.4461 | 0.085608
52 | 153 | 1.4445 | 0.086136
53 | 156 | 1.4429 | 0.086665
54 | 159 | 1.4414 | 0.087193
55 | 162 | 1.4399 | 0.087723
56 | 165 | 1.4385 | 0.088253
57 | 168 | 1.4372 | 0.088784
58 | 171 | 1.4359 | 0.089315
59 | 174 | 1.4346 | 0.089848
60 | 177 | 1.4335 | 0.090383
61 | 180 | 1.4324 | 0.090918
62 | 183 | 1.4313 | 0.091455
63 | 186 | 1.4303 | 0.091994
64 | 189 | 1.4294 | 0.092534
65 | 192 | 1.4285 | 0.093076
66 | 195 | 1.4277 | 0.09362
67 | 198 | 1.4269 | 0.094165
68 | 201 | 1.4262 | 0.094712
69 | 204 | 1.4255 | 0.095262
70 | 207 | 1.4249 | 0.095813
71 | 210 | 1.4244 | 0.096365
72 | 213 | 1.4239 | 0.09692
73 | 216 | 1.4234 | 0.097477
74 | 219 | 1.423 | 0.098036
75 | 222 | 1.4226 | 0.098596
76 | 225 | 1.4223 | 0.099158
77 | 228 | 1.422 | 0.099722
78 | 231 | 1.4218 | 0.10029
79 | 234 | 1.4215 | 0.10086
80 | 237 | 1.4214 | 0.10142
81 | 240 | 1.4212 | 0.102
82 | 243 | 1.4211 | 0.10257
83 | 246 | 1.421 | 0.10314
84 | 249 | 1.421 | 0.10372
85 | 252 | 1.421 | 0.10429
86 | 255 | 1.421 | 0.10487
87 | 258 | 1.421 | 0.10545
88 | 261 | 1.421 | 0.10603
89 | 264 | 1.4211 | 0.10661
90 | 267 | 1.4211 | 0.10719
91 | 270 | 1.4212 | 0.10777
92 | 273 | 1.4213 | 0.10836
93 | 276 | 1.4214 | 0.10894
94 | 279 | 1.4215 | 0.10952
95 | 282 | 1.4216 | 0.1101
96 | 285 | 1.4217 | 0.11069
97 | 288 | 1.4218 | 0.11127
98 | 291 | 1.4219 | 0.11185
99 | 294 | 1.422 | 0.11244
100 | 297 | 1.4221 | 0.11302
101 | 300 | 1.4222 | 0.1136
102 | 303 | 1.4222 | 0.11418
103 | 306 | 1.4223 | 0.11476
104 | 309 | 1.4223 | 0.11534
105 | 312 | 1.4223 | 0.11591
106 | 315 | 1.4223 | 0.11649
107 | 318 | 1.4222 | 0.11706
108 | 321 | 1.4221 | 0.11763
109 | 324 | 1.422 | 0.1182
110 | 327 | 1.4219 | 0.11877
111 | 330 | 1.4217 | 0.11933
112 | 333 | 1.4215 | 0.11989
113 | 336 | 1.4212 | 0.12045
114 | 339 | 1.4209 | 0.12101
115 | 342 | 1.4206 | 0.12156
116 | 345 | 1.4202 | 0.12211
117 | 348 | 1.4197 | 0.12265
118 | 351 | 1.4192 | 0.1232
119 | 354 | 1.4187 | 0.12373
120 | 357 | 1.418 | 0.12427
121 | 360 | 1.4174 | 0.1248
122 | 363 | 1.4166 | 0.12532
123 | 366 | 1.4158 | 0.12584
124 | 369 | 1.415 | 0.12636
125 | 372 | 1.4141 | 0.12687
126 | 375 | 1.4131 | 0.12737
127 | 378 | 1.412 | 0.12787
128 | 381 | 1.4109 | 0.12837
129 | 384 | 1.4097 | 0.12886
130 | 387 | 1.4084 | 0.12934
131 | 390 | 1.407 | 0.12982
132 | 393 | 1.4056 | 0.13029
133 | 396 | 1.4041 | 0.13075
134 | 399 | 1.4025 | 0.13121
135 | 402 | 1.4008 | 0.13166
136 | 405 | 1.399 | 0.1321
137 | 408 | 1.3971 | 0.13254
138 | 411 | 1.3952 | 0.13296
139 | 414 | 1.3931 | 0.13338
140 | 417 | 1.391 | 0.1338
141 | 420 | 1.3888 | 0.1342
142 | 423 | 1.3865 | 0.1346
143 | 426 | 1.3841 | 0.13499
144 | 429 | 1.3815 | 0.13537
145 | 432 | 1.3789 | 0.13574
146 | 435 | 1.3762 | 0.1361
147 | 438 | 1.3734 | 0.13646
148 | 441 | 1.3705 | 0.1368
149 | 444 | 1.3675 | 0.13714
150 | 447 | 1.3644 | 0.13747
151 | 450 | 1.3612 | 0.13778
152 | 453 | 1.3579 | 0.13809
153 | 456 | 1.3545 | 0.13839
154 | 459 | 1.351 | 0.13868
155 | 462 | 1.3474 | 0.13895
156 | 465 | 1.3436 | 0.13922
157 | 468 | 1.3398 | 0.13948
158 | 471 | 1.3359 | 0.13973
159 | 474 | 1.3318 | 0.13996
160 | 477 | 1.3277 | 0.14019
161 | 480 | 1.3234 | 0.1404
162 | 483 | 1.319 | 0.14061
163 | 486 | 1.3146 | 0.1408
164 | 489 | 1.31 | 0.14098
165 | 492 | 1.3053 | 0.14115
166 | 495 | 1.3005 | 0.14131
167 | 498 | 1.2956 | 0.14146
168 | 501 | 1.2906 | 0.1416
169 | 504 | 1.2855 | 0.14173
170 | 507 | 1.2803 | 0.14184
171 | 510 | 1.2749 | 0.14194
172 | 513 | 1.2695 | 0.14203
173 | 516 | 1.264 | 0.14211
174 | 519 | 1.2583 | 0.14218
175 | 522 | 1.2526 | 0.14223
176 | 525 | 1.2467 | 0.14228
177 | 528 | 1.2407 | 0.14231
178 | 531 | 1.2347 | 0.14233
179 | 534 | 1.2285 | 0.14233
180 | 537 | 1.2222 | 0.14233
181 | 540 | 1.2159 | 0.14231
182 | 543 | 1.2094 | 0.14228
183 | 546 | 1.2028 | 0.14224
184 | 549 | 1.1961 | 0.14219
185 | 552 | 1.1894 | 0.14212
186 | 555 | 1.1825 | 0.14204
187 | 558 | 1.1755 | 0.14195
188 | 561 | 1.1685 | 0.14185
189 | 564 | 1.1613 | 0.14173
190 | 567 | 1.1541 | 0.14161
191 | 570 | 1.1467 | 0.14147
192 | 573 | 1.1393 | 0.14132
193 | 576 | 1.1317 | 0.14115
194 | 579 | 1.1241 | 0.14098
195 | 582 | 1.1164 | 0.14079
196 | 585 | 1.1086 | 0.14059
197 | 588 | 1.1007 | 0.14037
198 | 591 | 1.0927 | 0.14015
199 | 594 | 1.0847 | 0.13991
200 | 597 | 1.0765 | 0.13967
201 | 600 | 1.0683 | 0.13941
202 | 603 | 1.06 | 0.13913
203 | 606 | 1.0516 | 0.13885
204 | 609 | 1.0431 | 0.13855
205 | 612 | 1.0346 | 0.13825
206 | 615 | 1.026 | 0.13793
207 | 618 | 1.0172 | 0.1376
208 | 621 | 1.0085 | 0.13726
209 | 624 | 0.9996 | 0.13691
210 | 627 | 0.99067 | 0.13655
211 | 630 | 0.98167 | 0.13617
212 | 633 | 0.97259 | 0.13579
213 | 636 | 0.96344 | 0.13539
214 | 639 | 0.95422 | 0.13499
215 | 642 | 0.94493 | 0.13457
216 | 645 | 0.93557 | 0.13414
217 | 648 | 0.92615 | 0.13371
218 | 651 | 0.91666 | 0.13326
219 | 654 | 0.9071 | 0.1328
220 | 657 | 0.89748 | 0.13233
221 | 660 | 0.88779 | 0.13186
222 | 663 | 0.87804 | 0.13137
223 | 666 | 0.86822 | 0.13088
224 | 669 | 0.85834 | 0.13037
225 | 672 | 0.8484 | 0.12986
226 | 675 | 0.8384 | 0.12934
227 | 678 | 0.82833 | 0.12881
228 | 681 | 0.8182 | 0.12827
229 | 684 | 0.80801 | 0.12772
230 | 687 | 0.79776 | 0.12716
231 | 690 | 0.78745 | 0.1266
232 | 693 | 0.77708 | 0.12603
233 | 696 | 0.76665 | 0.12545
234 | 699 | 0.75615 | 0.12487
235 | 702 | 0.74559 | 0.12427
236 | 705 | 0.73497 | 0.12367
237 | 708 | 0.72429 | 0.12307
238 | 711 | 0.71355 | 0.12245
239 | 714 | 0.70274 | 0.12183
240 | 717 | 0.69187 | 0.12121
241 | 720 | 0.68093 | 0.12058
242 | 723 | 0.66992 | 0.11994
243 | 726 | 0.65885 | 0.1193
244 | 729 | 0.64771 | 0.11866
245 | 732 | 0.6365 | 0.118
246 | 735 | 0.62522 | 0.11735
247 | 738 | 0.61386 | 0.11669
248 | 741 | 0.60243 | 0.11603
249 | 744 | 0.59093 | 0.11536
250 | 747 | 0.57934 | 0.11469
251 | 750 | 0.56768 | 0.11401
252 | 753 | 0.55593 | 0.11333
253 | 756 | 0.54409 | 0.11265
254 | 759 | 0.53217 | 0.11197
255 | 762 | 0.52016 | 0.11129
256 | 765 | 0.50805 | 0.1106
257 | 768 | 0.49585 | 0.10991
258 | 771 | 0.48354 | 0.10922
259 | 774 | 0.47114 | 0.10853
260 | 777 | 0.45862 | 0.10784
261 | 780 | 0.44599 | 0.10715
262 | 783 | 0.43325 | 0.10646
263 | 786 | 0.42039 | 0.10576
264 | 789 | 0.40741 | 0.10507
265 | 792 | 0.3943 | 0.10438
266 | 795 | 0.38105 | 0.10369
267 | 798 | 0.36766 | 0.103
268 | 801 | 0.35414 | 0.10231
269 | 804 | 0.34046 | 0.10163
270 | 807 | 0.32663 | 0.10094
271 | 810 | 0.31263 | 0.10026
272 | 813 | 0.29847 | 0.099582
273 | 816 | 0.28414 | 0.098906
274 | 819 | 0.26962 | 0.098234
275 | 822 | 0.25492 | 0.097564
276 | 825 | 0.24002 | 0.096899
277 | 828 | 0.22492 | 0.096238
278 | 831 | 0.20961 | 0.095581
279 | 834 | 0.19409 | 0.094929
280 | 837 | 0.17833 | 0.094282
281 | 840 | 0.16234 | 0.09364
282 | 843 | 0.14611 | 0.093004
283 | 846 | 0.12963 | 0.092373
284 | 849 | 0.11288 | 0.091749
285 | 852 | 0.095861 | 0.091132
286 | 855 | 0.078559 | 0.090521
287 | 858 | 0.060964 | 0.089917
288 | 861 | 0.043065 | 0.08932
289 | 864 | 0.024851 | 0.088731
290 | 867 | 0.0063118 | 0.08815
291 | 870 | -0.012566 | 0.087577 | 582

## 12-100 Data
12" Wheel Test | Date: 2/19/10 | Test #AMCA |  | Diameter In | Width % | Blade | Angle
| Test RPM | 1800 |  | 12.25 | 50 | 14.25 | 48 | HUNTAIR Wheel | 1800 | RPM
| CFM | SP | Power (BHP)
1 | 0 | 1.4715 | 0.075849 | [5 empty] | Motor HP
2 | 3 | 1.4734 | 0.077045 | [5 empty] | 0.001 | 0.5
3 | 6 | 1.4752 | 0.078228 | Speed (RPM) | 1800 |  |  |  | 0.5 | 0.5
4 | 9 | 1.477 | 0.079396 | Diameter | 12.25 |  |  |  | 0.51 | 0.75
5 | 12 | 1.4786 | 0.080551 | Width Factor* | 1 |  |  |  | 0.75 | 0.75
6 | 15 | 1.4802 | 0.081693 | *Note: Width Factor of 1 is 50% |  |  |  |  | 0.751 | 1
7 | 18 | 1.4817 | 0.082822 | [5 empty] | 1 | 1
8 | 21 | 1.4832 | 0.083938 | [5 empty] | 1.01 | 1.5
9 | 24 | 1.4846 | 0.085041 | Nominal | Actual |  |  |  | 1.5 | 1.5
10 | 27 | 1.4859 | 0.086132 | [5 empty] | 1.51 | 2
11 | 30 | 1.4871 | 0.087211 | 12 | 12.25 |  |  |  | 2 | 2
12 | 33 | 1.4882 | 0.088277 | 13 | N/A |  |  |  | 2.01 | 3
13 | 36 | 1.4893 | 0.089332 | 14 | 13.5 |  |  |  | 3 | 3
14 | 39 | 1.4904 | 0.090375 | 16 | 16.5 |  |  |  | 3.01 | 5
15 | 42 | 1.4913 | 0.091406 | 18 | 18.25 |  |  |  | 5 | 5
16 | 45 | 1.4922 | 0.092426 | 20 | 20 |  |  |  | 5.01 | 7.5
17 | 48 | 1.4931 | 0.093435 | 22 | 22.25 |  |  |  | 7.5 | 7.5
18 | 51 | 1.4938 | 0.094434 | [5 empty] | 7.51 | 10
19 | 54 | 1.4946 | 0.095421 | [5 empty] | 10 | 10
20 | 57 | 1.4952 | 0.096398 | [5 empty] | 10.01 | 15
21 | 60 | 1.4958 | 0.097364 | [5 empty] | 15 | 15
22 | 63 | 1.4964 | 0.09832 | [5 empty] | 15.01 | 20
23 | 66 | 1.4969 | 0.099266 | [5 empty] | 20 | 20
24 | 69 | 1.4973 | 0.1002 | [5 empty] | 20.01 | 25
25 | 72 | 1.4977 | 0.10113 | [5 empty] | 25 | 25
26 | 75 | 1.498 | 0.10205 | [5 empty] | 25.01 | 30
27 | 78 | 1.4983 | 0.10295 | [5 empty] | 30 | 30
28 | 81 | 1.4986 | 0.10385 | [5 empty] | 30.01 | 40
29 | 84 | 1.4988 | 0.10474 | [5 empty] | 40 | 40
30 | 87 | 1.499 | 0.10562 | [5 empty] | 40.01 | 50
31 | 90 | 1.4991 | 0.10649 | [5 empty] | 50 | 50
32 | 93 | 1.4991 | 0.10736 | [5 empty] | 50.01 | 60
33 | 96 | 1.4992 | 0.10821 | [5 empty] | 60 | 60
34 | 99 | 1.4992 | 0.10906 | [5 empty] | 60.01 | 75
35 | 102 | 1.4991 | 0.1099 | [5 empty] | 75 | 75
36 | 105 | 1.499 | 0.11073 | [5 empty] | 75.01 | 100
37 | 108 | 1.4989 | 0.11155 | [5 empty] | 100 | 100
38 | 111 | 1.4988 | 0.11237 | [5 empty] | 100.01 | 125
39 | 114 | 1.4986 | 0.11318 | [5 empty] | 125 | 125
40 | 117 | 1.4984 | 0.11398 | [5 empty] | 125.01 | 150
41 | 120 | 1.4981 | 0.11477 | [5 empty] | 150 | 150
42 | 123 | 1.4978 | 0.11556 | [5 empty] | 150.01 | 200
43 | 126 | 1.4975 | 0.11634 | [5 empty] | 200 | 200
44 | 129 | 1.4972 | 0.11711
45 | 132 | 1.4968 | 0.11788 | Equations Derived from AMCA Test Data Test No. 26668A-4
46 | 135 | 1.4964 | 0.11864 | Performance Equation
47 | 138 | 1.496 | 0.11939 | y = -5.30286453E-19x6 + 3.98191270E-15x5 - 1.01173678E-11x4 + 1.05262420E-08x3 - 4.71801092E-06x2 + 6.53398493E-04x + 1.47145132E+00
48 | 141 | 1.4955 | 0.12014 | Power Equation
49 | 144 | 1.495 | 0.12088 | y = -3.71860883E-22x6 + 2.33655295E-16x5 - 9.78327567E-13x4 + 1.32212729E-09x3 - 7.84489673E-07x2 + 4.01100685E-04x + 7.58489901E-02
50 | 147 | 1.4945 | 0.12162
51 | 150 | 1.494 | 0.12235
52 | 153 | 1.4935 | 0.12307
53 | 156 | 1.4929 | 0.12379
54 | 159 | 1.4923 | 0.1245
55 | 162 | 1.4917 | 0.12521
56 | 165 | 1.4911 | 0.12592
57 | 168 | 1.4904 | 0.12661
58 | 171 | 1.4898 | 0.12731
59 | 174 | 1.4891 | 0.12799
60 | 177 | 1.4884 | 0.12868
61 | 180 | 1.4877 | 0.12936
62 | 183 | 1.487 | 0.13003
63 | 186 | 1.4862 | 0.1307
64 | 189 | 1.4855 | 0.13137
65 | 192 | 1.4847 | 0.13203
66 | 195 | 1.484 | 0.13269
67 | 198 | 1.4832 | 0.13334
68 | 201 | 1.4824 | 0.13399
69 | 204 | 1.4816 | 0.13464
70 | 207 | 1.4808 | 0.13528
71 | 210 | 1.48 | 0.13592
72 | 213 | 1.4792 | 0.13656
73 | 216 | 1.4783 | 0.13719
74 | 219 | 1.4775 | 0.13782
75 | 222 | 1.4767 | 0.13845
76 | 225 | 1.4758 | 0.13907
77 | 228 | 1.475 | 0.13969
78 | 231 | 1.4741 | 0.14031
79 | 234 | 1.4733 | 0.14092
80 | 237 | 1.4724 | 0.14153
81 | 240 | 1.4715 | 0.14214
82 | 243 | 1.4707 | 0.14275
83 | 246 | 1.4698 | 0.14336
84 | 249 | 1.4689 | 0.14396
85 | 252 | 1.4681 | 0.14456
86 | 255 | 1.4672 | 0.14516
87 | 258 | 1.4663 | 0.14575
88 | 261 | 1.4655 | 0.14635
89 | 264 | 1.4646 | 0.14694
90 | 267 | 1.4637 | 0.14753
91 | 270 | 1.4629 | 0.14812
92 | 273 | 1.462 | 0.1487
93 | 276 | 1.4611 | 0.14929
94 | 279 | 1.4603 | 0.14987
95 | 282 | 1.4594 | 0.15045
96 | 285 | 1.4586 | 0.15103
97 | 288 | 1.4577 | 0.15161
98 | 291 | 1.4569 | 0.15219
99 | 294 | 1.4561 | 0.15277
100 | 297 | 1.4552 | 0.15334
101 | 300 | 1.4544 | 0.15392
102 | 303 | 1.4536 | 0.15449
103 | 306 | 1.4528 | 0.15506
104 | 309 | 1.452 | 0.15563
105 | 312 | 1.4512 | 0.1562
106 | 315 | 1.4504 | 0.15677
107 | 318 | 1.4496 | 0.15734
108 | 321 | 1.4488 | 0.15791
109 | 324 | 1.448 | 0.15847
110 | 327 | 1.4472 | 0.15904
111 | 330 | 1.4465 | 0.15961
112 | 333 | 1.4457 | 0.16017
113 | 336 | 1.445 | 0.16074
114 | 339 | 1.4442 | 0.1613
115 | 342 | 1.4435 | 0.16186
116 | 345 | 1.4428 | 0.16243
117 | 348 | 1.4421 | 0.16299
118 | 351 | 1.4414 | 0.16355
119 | 354 | 1.4407 | 0.16412
120 | 357 | 1.44 | 0.16468
121 | 360 | 1.4393 | 0.16524
122 | 363 | 1.4387 | 0.1658
123 | 366 | 1.438 | 0.16636
124 | 369 | 1.4373 | 0.16693
125 | 372 | 1.4367 | 0.16749
126 | 375 | 1.4361 | 0.16805
127 | 378 | 1.4355 | 0.16861
128 | 381 | 1.4348 | 0.16917
129 | 384 | 1.4342 | 0.16973
130 | 387 | 1.4337 | 0.1703
131 | 390 | 1.4331 | 0.17086
132 | 393 | 1.4325 | 0.17142
133 | 396 | 1.4319 | 0.17198
134 | 399 | 1.4314 | 0.17255
135 | 402 | 1.4308 | 0.17311
136 | 405 | 1.4303 | 0.17367
137 | 408 | 1.4298 | 0.17423
138 | 411 | 1.4293 | 0.1748
139 | 414 | 1.4288 | 0.17536
140 | 417 | 1.4283 | 0.17593
141 | 420 | 1.4278 | 0.17649
142 | 423 | 1.4273 | 0.17705
143 | 426 | 1.4269 | 0.17762
144 | 429 | 1.4264 | 0.17819
145 | 432 | 1.426 | 0.17875
146 | 435 | 1.4255 | 0.17932
147 | 438 | 1.4251 | 0.17988
148 | 441 | 1.4247 | 0.18045
149 | 444 | 1.4243 | 0.18102
150 | 447 | 1.4239 | 0.18159
151 | 450 | 1.4235 | 0.18215
152 | 453 | 1.4231 | 0.18272
153 | 456 | 1.4227 | 0.18329
154 | 459 | 1.4224 | 0.18386
155 | 462 | 1.422 | 0.18443
156 | 465 | 1.4217 | 0.185
157 | 468 | 1.4213 | 0.18557
158 | 471 | 1.421 | 0.18615
159 | 474 | 1.4207 | 0.18672
160 | 477 | 1.4204 | 0.18729
161 | 480 | 1.4201 | 0.18786
162 | 483 | 1.4198 | 0.18844
163 | 486 | 1.4195 | 0.18901
164 | 489 | 1.4192 | 0.18958
165 | 492 | 1.4189 | 0.19016
166 | 495 | 1.4187 | 0.19073
167 | 498 | 1.4184 | 0.19131
168 | 501 | 1.4182 | 0.19189
169 | 504 | 1.4179 | 0.19246
170 | 507 | 1.4177 | 0.19304
171 | 510 | 1.4174 | 0.19362
172 | 513 | 1.4172 | 0.19419
173 | 516 | 1.417 | 0.19477
174 | 519 | 1.4168 | 0.19535
175 | 522 | 1.4166 | 0.19593
176 | 525 | 1.4164 | 0.19651
177 | 528 | 1.4162 | 0.19709
178 | 531 | 1.416 | 0.19767
179 | 534 | 1.4158 | 0.19824
180 | 537 | 1.4156 | 0.19882
181 | 540 | 1.4154 | 0.19941
182 | 543 | 1.4152 | 0.19999
183 | 546 | 1.4151 | 0.20057
184 | 549 | 1.4149 | 0.20115
185 | 552 | 1.4147 | 0.20173
186 | 555 | 1.4146 | 0.20231
187 | 558 | 1.4144 | 0.20289
188 | 561 | 1.4143 | 0.20347
189 | 564 | 1.4141 | 0.20405
190 | 567 | 1.414 | 0.20464
191 | 570 | 1.4138 | 0.20522
192 | 573 | 1.4137 | 0.2058
193 | 576 | 1.4135 | 0.20638
194 | 579 | 1.4134 | 0.20696
195 | 582 | 1.4132 | 0.20755
196 | 585 | 1.4131 | 0.20813
197 | 588 | 1.4129 | 0.20871
198 | 591 | 1.4128 | 0.20929
199 | 594 | 1.4126 | 0.20987
200 | 597 | 1.4125 | 0.21045
201 | 600 | 1.4124 | 0.21103
202 | 603 | 1.4122 | 0.21161
203 | 606 | 1.4121 | 0.21219
204 | 609 | 1.4119 | 0.21277
205 | 612 | 1.4118 | 0.21335
206 | 615 | 1.4116 | 0.21393
207 | 618 | 1.4115 | 0.21451
208 | 621 | 1.4113 | 0.21509
209 | 624 | 1.4111 | 0.21567
210 | 627 | 1.411 | 0.21625
211 | 630 | 1.4108 | 0.21682
212 | 633 | 1.4106 | 0.2174
213 | 636 | 1.4105 | 0.21797
214 | 639 | 1.4103 | 0.21855
215 | 642 | 1.4101 | 0.21912
216 | 645 | 1.4099 | 0.2197
217 | 648 | 1.4097 | 0.22027
218 | 651 | 1.4095 | 0.22084
219 | 654 | 1.4093 | 0.22141
220 | 657 | 1.4091 | 0.22198
221 | 660 | 1.4089 | 0.22255
222 | 663 | 1.4086 | 0.22312
223 | 666 | 1.4084 | 0.22369
224 | 669 | 1.4082 | 0.22426
225 | 672 | 1.4079 | 0.22482
226 | 675 | 1.4077 | 0.22539
227 | 678 | 1.4074 | 0.22595
228 | 681 | 1.4071 | 0.22651
229 | 684 | 1.4068 | 0.22707
230 | 687 | 1.4066 | 0.22763
231 | 690 | 1.4063 | 0.22819
232 | 693 | 1.4059 | 0.22875
233 | 696 | 1.4056 | 0.2293
234 | 699 | 1.4053 | 0.22986
235 | 702 | 1.4049 | 0.23041
236 | 705 | 1.4046 | 0.23096
237 | 708 | 1.4042 | 0.23151
238 | 711 | 1.4039 | 0.23206
239 | 714 | 1.4035 | 0.2326
240 | 717 | 1.4031 | 0.23315
241 | 720 | 1.4026 | 0.23369
242 | 723 | 1.4022 | 0.23423
243 | 726 | 1.4018 | 0.23477
244 | 729 | 1.4013 | 0.2353
245 | 732 | 1.4009 | 0.23584
246 | 735 | 1.4004 | 0.23637
247 | 738 | 1.3999 | 0.2369
248 | 741 | 1.3994 | 0.23743
249 | 744 | 1.3988 | 0.23796
250 | 747 | 1.3983 | 0.23848
251 | 750 | 1.3977 | 0.239
252 | 753 | 1.3972 | 0.23952
253 | 756 | 1.3966 | 0.24004
254 | 759 | 1.3959 | 0.24056
255 | 762 | 1.3953 | 0.24107
256 | 765 | 1.3947 | 0.24158
257 | 768 | 1.394 | 0.24209
258 | 771 | 1.3933 | 0.24259
259 | 774 | 1.3926 | 0.24309
260 | 777 | 1.3919 | 0.24359
261 | 780 | 1.3912 | 0.24409
262 | 783 | 1.3904 | 0.24458
263 | 786 | 1.3897 | 0.24508
264 | 789 | 1.3889 | 0.24556
265 | 792 | 1.3881 | 0.24605
266 | 795 | 1.3872 | 0.24653
267 | 798 | 1.3864 | 0.24701
268 | 801 | 1.3855 | 0.24749
269 | 804 | 1.3846 | 0.24796
270 | 807 | 1.3837 | 0.24843
271 | 810 | 1.3827 | 0.2489
272 | 813 | 1.3818 | 0.24936
273 | 816 | 1.3808 | 0.24982
274 | 819 | 1.3798 | 0.25028
275 | 822 | 1.3788 | 0.25073
276 | 825 | 1.3777 | 0.25118
277 | 828 | 1.3766 | 0.25163
278 | 831 | 1.3755 | 0.25207
279 | 834 | 1.3744 | 0.25251
280 | 837 | 1.3732 | 0.25294
281 | 840 | 1.3721 | 0.25337
282 | 843 | 1.3709 | 0.2538
283 | 846 | 1.3696 | 0.25422
284 | 849 | 1.3684 | 0.25464
285 | 852 | 1.3671 | 0.25506
286 | 855 | 1.3658 | 0.25547
287 | 858 | 1.3645 | 0.25588
288 | 861 | 1.3631 | 0.25628
289 | 864 | 1.3618 | 0.25668
290 | 867 | 1.3603 | 0.25708
291 | 870 | 1.3589 | 0.25747
292 | 873 | 1.3575 | 0.25785
293 | 876 | 1.356 | 0.25824
294 | 879 | 1.3544 | 0.25861
295 | 882 | 1.3529 | 0.25899
296 | 885 | 1.3513 | 0.25935
297 | 888 | 1.3497 | 0.25972
298 | 891 | 1.3481 | 0.26008
299 | 894 | 1.3464 | 0.26043
300 | 897 | 1.3447 | 0.26078
301 | 900 | 1.343 | 0.26113
302 | 903 | 1.3413 | 0.26147
303 | 906 | 1.3395 | 0.2618
304 | 909 | 1.3377 | 0.26213
305 | 912 | 1.3358 | 0.26246
306 | 915 | 1.334 | 0.26278
307 | 918 | 1.3321 | 0.26309
308 | 921 | 1.3301 | 0.2634
309 | 924 | 1.3281 | 0.26371
310 | 927 | 1.3262 | 0.26401
311 | 930 | 1.3241 | 0.2643
312 | 933 | 1.3221 | 0.26459
313 | 936 | 1.32 | 0.26487
314 | 939 | 1.3178 | 0.26515
315 | 942 | 1.3157 | 0.26542
316 | 945 | 1.3135 | 0.26569
317 | 948 | 1.3113 | 0.26595
318 | 951 | 1.309 | 0.26621
319 | 954 | 1.3067 | 0.26646
320 | 957 | 1.3044 | 0.2667
321 | 960 | 1.302 | 0.26694
322 | 963 | 1.2997 | 0.26717
323 | 966 | 1.2972 | 0.2674
324 | 969 | 1.2948 | 0.26762
325 | 972 | 1.2923 | 0.26783
326 | 975 | 1.2898 | 0.26804
327 | 978 | 1.2872 | 0.26825
328 | 981 | 1.2846 | 0.26844
329 | 984 | 1.282 | 0.26863
330 | 987 | 1.2793 | 0.26882
331 | 990 | 1.2766 | 0.269
332 | 993 | 1.2739 | 0.26917
333 | 996 | 1.2711 | 0.26933
334 | 999 | 1.2683 | 0.26949
335 | 1002 | 1.2654 | 0.26964
336 | 1005 | 1.2626 | 0.26979
337 | 1008 | 1.2596 | 0.26993
338 | 1011 | 1.2567 | 0.27006
339 | 1014 | 1.2537 | 0.27019
340 | 1017 | 1.2507 | 0.27031
341 | 1020 | 1.2476 | 0.27042
342 | 1023 | 1.2445 | 0.27053
343 | 1026 | 1.2414 | 0.27063
344 | 1029 | 1.2382 | 0.27072
345 | 1032 | 1.235 | 0.27081
346 | 1035 | 1.2318 | 0.27089
347 | 1038 | 1.2285 | 0.27096
348 | 1041 | 1.2252 | 0.27103
349 | 1044 | 1.2219 | 0.27108
350 | 1047 | 1.2185 | 0.27114
351 | 1050 | 1.215 | 0.27118
352 | 1053 | 1.2116 | 0.27122
353 | 1056 | 1.2081 | 0.27125
354 | 1059 | 1.2045 | 0.27127
355 | 1062 | 1.201 | 0.27129
356 | 1065 | 1.1974 | 0.2713
357 | 1068 | 1.1937 | 0.2713
358 | 1071 | 1.19 | 0.27129
359 | 1074 | 1.1863 | 0.27128
360 | 1077 | 1.1825 | 0.27126
361 | 1080 | 1.1787 | 0.27123
362 | 1083 | 1.1749 | 0.2712
363 | 1086 | 1.171 | 0.27115
364 | 1089 | 1.1671 | 0.2711
365 | 1092 | 1.1632 | 0.27105
366 | 1095 | 1.1592 | 0.27098
367 | 1098 | 1.1552 | 0.27091
368 | 1101 | 1.1511 | 0.27083
369 | 1104 | 1.147 | 0.27074
370 | 1107 | 1.1429 | 0.27064
371 | 1110 | 1.1387 | 0.27054
372 | 1113 | 1.1345 | 0.27043
373 | 1116 | 1.1302 | 0.27031
374 | 1119 | 1.126 | 0.27018
375 | 1122 | 1.1216 | 0.27005
376 | 1125 | 1.1173 | 0.26991
377 | 1128 | 1.1129 | 0.26976
378 | 1131 | 1.1084 | 0.2696
379 | 1134 | 1.104 | 0.26944
380 | 1137 | 1.0995 | 0.26926
381 | 1140 | 1.0949 | 0.26908
382 | 1143 | 1.0903 | 0.26889
383 | 1146 | 1.0857 | 0.2687
384 | 1149 | 1.0811 | 0.26849
385 | 1152 | 1.0764 | 0.26828
386 | 1155 | 1.0717 | 0.26806
387 | 1158 | 1.0669 | 0.26783
388 | 1161 | 1.0621 | 0.26759
389 | 1164 | 1.0573 | 0.26735
390 | 1167 | 1.0524 | 0.26709
391 | 1170 | 1.0475 | 0.26683
392 | 1173 | 1.0425 | 0.26656
393 | 1176 | 1.0375 | 0.26629
394 | 1179 | 1.0325 | 0.266
395 | 1182 | 1.0275 | 0.26571
396 | 1185 | 1.0224 | 0.26541
397 | 1188 | 1.0173 | 0.2651
398 | 1191 | 1.0121 | 0.26478
399 | 1194 | 1.0069 | 0.26445
400 | 1197 | 1.0017 | 0.26412
401 | 1200 | 0.99641 | 0.26378
402 | 1203 | 0.99111 | 0.26343
403 | 1206 | 0.98578 | 0.26307
404 | 1209 | 0.98041 | 0.26271
405 | 1212 | 0.97501 | 0.26233
406 | 1215 | 0.96958 | 0.26195
407 | 1218 | 0.96411 | 0.26156
408 | 1221 | 0.95861 | 0.26116
409 | 1224 | 0.95307 | 0.26075
410 | 1227 | 0.9475 | 0.26034
411 | 1230 | 0.9419 | 0.25991
412 | 1233 | 0.93626 | 0.25948
413 | 1236 | 0.93059 | 0.25904
414 | 1239 | 0.92489 | 0.2586
415 | 1242 | 0.91916 | 0.25814
416 | 1245 | 0.9134 | 0.25768
417 | 1248 | 0.9076 | 0.2572
418 | 1251 | 0.90177 | 0.25672
419 | 1254 | 0.89591 | 0.25624
420 | 1257 | 0.89002 | 0.25574
421 | 1260 | 0.8841 | 0.25524
422 | 1263 | 0.87815 | 0.25472
423 | 1266 | 0.87217 | 0.2542
424 | 1269 | 0.86616 | 0.25368
425 | 1272 | 0.86012 | 0.25314
426 | 1275 | 0.85405 | 0.2526
427 | 1278 | 0.84795 | 0.25204
428 | 1281 | 0.84182 | 0.25148
429 | 1284 | 0.83566 | 0.25092
430 | 1287 | 0.82947 | 0.25034
431 | 1290 | 0.82326 | 0.24976
432 | 1293 | 0.81701 | 0.24917
433 | 1296 | 0.81074 | 0.24857
434 | 1299 | 0.80445 | 0.24796
435 | 1302 | 0.79812 | 0.24734
436 | 1305 | 0.79177 | 0.24672
437 | 1308 | 0.78539 | 0.24609
438 | 1311 | 0.77899 | 0.24545
439 | 1314 | 0.77256 | 0.24481
440 | 1317 | 0.76611 | 0.24416
441 | 1320 | 0.75963 | 0.24349
442 | 1323 | 0.75313 | 0.24283
443 | 1326 | 0.7466 | 0.24215
444 | 1329 | 0.74004 | 0.24147
445 | 1332 | 0.73347 | 0.24078
446 | 1335 | 0.72687 | 0.24008
447 | 1338 | 0.72025 | 0.23937
448 | 1341 | 0.7136 | 0.23866
449 | 1344 | 0.70694 | 0.23794
450 | 1347 | 0.70025 | 0.23721
451 | 1350 | 0.69354 | 0.23648
452 | 1353 | 0.68681 | 0.23574
453 | 1356 | 0.68005 | 0.23499
454 | 1359 | 0.67328 | 0.23423
455 | 1362 | 0.66649 | 0.23347
456 | 1365 | 0.65968 | 0.2327
457 | 1368 | 0.65285 | 0.23192
458 | 1371 | 0.646 | 0.23114
459 | 1374 | 0.63913 | 0.23035
460 | 1377 | 0.63224 | 0.22955
461 | 1380 | 0.62534 | 0.22875
462 | 1383 | 0.61842 | 0.22793
463 | 1386 | 0.61148 | 0.22712
464 | 1389 | 0.60453 | 0.22629
465 | 1392 | 0.59756 | 0.22546
466 | 1395 | 0.59058 | 0.22463
467 | 1398 | 0.58358 | 0.22378
468 | 1401 | 0.57657 | 0.22293
469 | 1404 | 0.56954 | 0.22208
470 | 1407 | 0.5625 | 0.22122
471 | 1410 | 0.55545 | 0.22035
472 | 1413 | 0.54838 | 0.21948
473 | 1416 | 0.5413 | 0.2186
474 | 1419 | 0.53421 | 0.21771
475 | 1422 | 0.52711 | 0.21682
476 | 1425 | 0.52 | 0.21592
477 | 1428 | 0.51288 | 0.21502
478 | 1431 | 0.50575 | 0.21411
479 | 1434 | 0.49861 | 0.2132
480 | 1437 | 0.49146 | 0.21228
481 | 1440 | 0.4843 | 0.21135
482 | 1443 | 0.47714 | 0.21042
483 | 1446 | 0.46997 | 0.20949
484 | 1449 | 0.46279 | 0.20855
485 | 1452 | 0.45561 | 0.2076
486 | 1455 | 0.44842 | 0.20665
487 | 1458 | 0.44122 | 0.2057
488 | 1461 | 0.43402 | 0.20474
489 | 1464 | 0.42682 | 0.20378
490 | 1467 | 0.41961 | 0.20281
491 | 1470 | 0.4124 | 0.20183
492 | 1473 | 0.40519 | 0.20086
493 | 1476 | 0.39798 | 0.19987
494 | 1479 | 0.39076 | 0.19889
495 | 1482 | 0.38355 | 0.1979
496 | 1485 | 0.37633 | 0.1969
497 | 1488 | 0.36912 | 0.19591
498 | 1491 | 0.3619 | 0.19491
499 | 1494 | 0.35469 | 0.1939
500 | 1497 | 0.34748 | 0.19289
501 | 1500 | 0.34027 | 0.19188
502 | 1503 | 0.33307 | 0.19086
503 | 1506 | 0.32587 | 0.18984
504 | 1509 | 0.31867 | 0.18882
505 | 1512 | 0.31148 | 0.1878
506 | 1515 | 0.3043 | 0.18677
507 | 1518 | 0.29712 | 0.18574
508 | 1521 | 0.28995 | 0.18471
509 | 1524 | 0.28278 | 0.18367
510 | 1527 | 0.27563 | 0.18263
511 | 1530 | 0.26848 | 0.18159
512 | 1533 | 0.26134 | 0.18055
513 | 1536 | 0.25421 | 0.17951
514 | 1539 | 0.2471 | 0.17846
515 | 1542 | 0.23999 | 0.17741
516 | 1545 | 0.2329 | 0.17636
517 | 1548 | 0.22582 | 0.17531
518 | 1551 | 0.21875 | 0.17426
519 | 1554 | 0.21169 | 0.1732
520 | 1557 | 0.20466 | 0.17215
521 | 1560 | 0.19763 | 0.17109
522 | 1563 | 0.19062 | 0.17004
523 | 1566 | 0.18363 | 0.16898
524 | 1569 | 0.17665 | 0.16792
525 | 1572 | 0.1697 | 0.16686
526 | 1575 | 0.16276 | 0.1658
527 | 1578 | 0.15584 | 0.16475
528 | 1581 | 0.14894 | 0.16369
529 | 1584 | 0.14206 | 0.16263
530 | 1587 | 0.1352 | 0.16157
531 | 1590 | 0.12836 | 0.16052
532 | 1593 | 0.12155 | 0.15946
533 | 1596 | 0.11476 | 0.1584
534 | 1599 | 0.10799 | 0.15735
535 | 1602 | 0.10124 | 0.15629
536 | 1605 | 0.094527 | 0.15524
537 | 1608 | 0.087835 | 0.15419
538 | 1611 | 0.081169 | 0.15314
539 | 1614 | 0.074531 | 0.1521
540 | 1617 | 0.067921 | 0.15105
541 | 1620 | 0.06134 | 0.15001
542 | 1623 | 0.054788 | 0.14897
543 | 1626 | 0.048266 | 0.14793
544 | 1629 | 0.041775 | 0.14689
545 | 1632 | 0.035316 | 0.14586
546 | 1635 | 0.028889 | 0.14483
547 | 1638 | 0.022495 | 0.14381
548 | 1641 | 0.016135 | 0.14278
549 | 1644 | 0.0098087 | 0.14177
550 | 1647 | 0.0035179 | 0.14075
551 | 1650 | -0.0027369 | 0.13974
552 | 1653 | -0.0089551 | 0.13873
553 | 1656 | -0.015136 | 0.13773
554 | 1659 | -0.021279 | 0.13673
555 | 1662 | -0.027383 | 0.13574
556 | 1665 | -0.033447 | 0.13475
557 | 1668 | -0.039471 | 0.13377
558 | 1671 | -0.045454 | 0.13279
559 | 1674 | -0.051395 | 0.13182
560 | 1677 | -0.057294 | 0.13085
561 | 1680 | -0.063149 | 0.12989
562 | 1683 | -0.068961 | 0.12894
563 | 1686 | -0.074727 | 0.12799
564 | 1689 | -0.080448 | 0.12705
565 | 1692 | -0.086123 | 0.12612
566 | 1695 | -0.09175 | 0.12519
567 | 1698 | -0.09733 | 0.12427
568 | 1701 | -0.10286 | 0.12336
569 | 1704 | -0.10834 | 0.12245
570 | 1707 | -0.11378 | 0.12156
571 | 1710 | -0.11916 | 0.12067
572 | 1713 | -0.12449 | 0.11979
573 | 1716 | -0.12976 | 0.11892
574 | 1719 | -0.13499 | 0.11806
575 | 1722 | -0.14016 | 0.11721
576 | 1725 | -0.14527 | 0.11636
577 | 1728 | -0.15033 | 0.11553
578 | 1731 | -0.15533 | 0.11471
579 | 1734 | -0.16028 | 0.11389
580 | 1737 | -0.16517 | 0.11309
581 | 1740 | -0.17 | 0.1123
582 | 1743 | -0.17477 | 0.11151

## Curve Tables
Fan Wheel Size 12-50
Operating Curve Data Points
|  |  | 1800 |  | RPM
| CFM | SP | BHP | BHP | Efficiency
|  |  | TOTAL | PER FAN
1 | 0 | 1.5307 | 0.10201 | 0.10201 | 0
2 | 6 | 1.5315 | 0.1042 | 0.1042 | 1.3863
3 | 12 | 1.532 | 0.10633 | 0.10633 | 2.7179
4 | 18 | 1.5323 | 0.10841 | 0.10841 | 3.9997
5 | 24 | 1.5324 | 0.11042 | 0.11042 | 5.2357
6 | 30 | 1.5323 | 0.11239 | 0.11239 | 6.4295
7 | 36 | 1.5319 | 0.1143 | 0.1143 | 7.5846
8 | 42 | 1.5313 | 0.11616 | 0.11616 | 8.7036
9 | 48 | 1.5306 | 0.11798 | 0.11798 | 9.7892
10 | 54 | 1.5297 | 0.11975 | 0.11975 | 10.8437
11 | 60 | 1.5286 | 0.12148 | 0.12148 | 11.869
12 | 66 | 1.5274 | 0.12316 | 0.12316 | 12.8672
13 | 72 | 1.5261 | 0.12481 | 0.12481 | 13.8397
14 | 78 | 1.5246 | 0.12641 | 0.12641 | 14.7882
15 | 84 | 1.523 | 0.12798 | 0.12798 | 15.714
16 | 90 | 1.5213 | 0.12952 | 0.12952 | 16.6183
17 | 96 | 1.5195 | 0.13102 | 0.13102 | 17.5023
18 | 102 | 1.5176 | 0.13249 | 0.13249 | 18.3669
19 | 108 | 1.5156 | 0.13393 | 0.13393 | 19.2133
20 | 114 | 1.5136 | 0.13534 | 0.13534 | 20.0422
21 | 120 | 1.5115 | 0.13672 | 0.13672 | 20.8544
22 | 126 | 1.5093 | 0.13808 | 0.13808 | 21.6506
23 | 132 | 1.5071 | 0.13941 | 0.13941 | 22.4316
24 | 138 | 1.5048 | 0.14072 | 0.14072 | 23.198
25 | 144 | 1.5025 | 0.14201 | 0.14201 | 23.9503
26 | 150 | 1.5002 | 0.14328 | 0.14328 | 24.6891
27 | 156 | 1.4978 | 0.14453 | 0.14453 | 25.4149
28 | 162 | 1.4955 | 0.14576 | 0.14576 | 26.1281
29 | 168 | 1.4931 | 0.14697 | 0.14697 | 26.8293
30 | 174 | 1.4907 | 0.14817 | 0.14817 | 27.5188
31 | 180 | 1.4883 | 0.14935 | 0.14935 | 28.197
32 | 186 | 1.4859 | 0.15052 | 0.15052 | 28.8643
33 | 192 | 1.4835 | 0.15168 | 0.15168 | 29.5209
34 | 198 | 1.4812 | 0.15282 | 0.15282 | 30.1673
35 | 204 | 1.4788 | 0.15395 | 0.15395 | 30.8038
36 | 210 | 1.4765 | 0.15508 | 0.15508 | 31.4305
37 | 216 | 1.4742 | 0.15619 | 0.15619 | 32.0479
38 | 222 | 1.4719 | 0.15729 | 0.15729 | 32.6561
39 | 228 | 1.4696 | 0.15839 | 0.15839 | 33.2554
40 | 234 | 1.4674 | 0.15948 | 0.15948 | 33.846
41 | 240 | 1.4652 | 0.16057 | 0.16057 | 34.4282
42 | 246 | 1.4631 | 0.16164 | 0.16164 | 35.0022
43 | 252 | 1.461 | 0.16272 | 0.16272 | 35.5681
44 | 258 | 1.4589 | 0.16379 | 0.16379 | 36.1262
45 | 264 | 1.4569 | 0.16485 | 0.16485 | 36.6767
46 | 270 | 1.455 | 0.16592 | 0.16592 | 37.2197
47 | 276 | 1.453 | 0.16698 | 0.16698 | 37.7555
48 | 282 | 1.4512 | 0.16804 | 0.16804 | 38.2841
49 | 288 | 1.4494 | 0.1691 | 0.1691 | 38.8058
50 | 294 | 1.4476 | 0.17015 | 0.17015 | 39.3207
51 | 300 | 1.4459 | 0.17121 | 0.17121 | 39.8289
52 | 306 | 1.4443 | 0.17226 | 0.17226 | 40.3306
53 | 312 | 1.4427 | 0.17332 | 0.17332 | 40.826
54 | 318 | 1.4412 | 0.17438 | 0.17438 | 41.3151
55 | 324 | 1.4397 | 0.17544 | 0.17544 | 41.7982
56 | 330 | 1.4383 | 0.1765 | 0.1765 | 42.2752
57 | 336 | 1.437 | 0.17756 | 0.17756 | 42.7465
58 | 342 | 1.4357 | 0.17862 | 0.17862 | 43.212
59 | 348 | 1.4345 | 0.17969 | 0.17969 | 43.6719
60 | 354 | 1.4333 | 0.18076 | 0.18076 | 44.1263
61 | 360 | 1.4322 | 0.18183 | 0.18183 | 44.5753
62 | 366 | 1.4311 | 0.1829 | 0.1829 | 45.0191
63 | 372 | 1.4301 | 0.18398 | 0.18398 | 45.4576
64 | 378 | 1.4292 | 0.18506 | 0.18506 | 45.8911
65 | 384 | 1.4283 | 0.18614 | 0.18614 | 46.3196
66 | 390 | 1.4275 | 0.18723 | 0.18723 | 46.7433
67 | 396 | 1.4267 | 0.18832 | 0.18832 | 47.1621
68 | 402 | 1.426 | 0.18942 | 0.18942 | 47.5762
69 | 408 | 1.4254 | 0.19051 | 0.19051 | 47.9857
70 | 414 | 1.4248 | 0.19162 | 0.19162 | 48.3907
71 | 420 | 1.4242 | 0.19272 | 0.19272 | 48.7912
72 | 426 | 1.4237 | 0.19383 | 0.19383 | 49.1873
73 | 432 | 1.4232 | 0.19494 | 0.19494 | 49.5792
74 | 438 | 1.4228 | 0.19606 | 0.19606 | 49.9668
75 | 444 | 1.4224 | 0.19718 | 0.19718 | 50.3502
76 | 450 | 1.4221 | 0.19831 | 0.19831 | 50.7295
77 | 456 | 1.4218 | 0.19944 | 0.19944 | 51.1048
78 | 462 | 1.4216 | 0.20057 | 0.20057 | 51.4762
79 | 468 | 1.4214 | 0.2017 | 0.2017 | 51.8436
80 | 474 | 1.4212 | 0.20284 | 0.20284 | 52.2072
81 | 480 | 1.4211 | 0.20398 | 0.20398 | 52.567
82 | 486 | 1.4209 | 0.20513 | 0.20513 | 52.9231
83 | 492 | 1.4209 | 0.20627 | 0.20627 | 53.2755
84 | 498 | 1.4208 | 0.20742 | 0.20742 | 53.6242
85 | 504 | 1.4208 | 0.20858 | 0.20858 | 53.9694
86 | 510 | 1.4208 | 0.20973 | 0.20973 | 54.3111
87 | 516 | 1.4208 | 0.21089 | 0.21089 | 54.6492
88 | 522 | 1.4208 | 0.21205 | 0.21205 | 54.9839
89 | 528 | 1.4209 | 0.21321 | 0.21321 | 55.3152
90 | 534 | 1.421 | 0.21437 | 0.21437 | 55.6431
91 | 540 | 1.421 | 0.21553 | 0.21553 | 55.9677
92 | 546 | 1.4211 | 0.2167 | 0.2167 | 56.289
93 | 552 | 1.4212 | 0.21787 | 0.21787 | 56.607
94 | 558 | 1.4213 | 0.21903 | 0.21903 | 56.9217
95 | 564 | 1.4214 | 0.2202 | 0.2202 | 57.2333
96 | 570 | 1.4216 | 0.22136 | 0.22136 | 57.5417
97 | 576 | 1.4217 | 0.22253 | 0.22253 | 57.8469
98 | 582 | 1.4218 | 0.2237 | 0.2237 | 58.149
99 | 588 | 1.4218 | 0.22486 | 0.22486 | 58.448
100 | 594 | 1.4219 | 0.22602 | 0.22602 | 58.7439
101 | 600 | 1.422 | 0.22719 | 0.22719 | 59.0367
102 | 606 | 1.4221 | 0.22835 | 0.22835 | 59.3265
103 | 612 | 1.4221 | 0.2295 | 0.2295 | 59.6132
104 | 618 | 1.4221 | 0.23066 | 0.23066 | 59.897
105 | 624 | 1.4221 | 0.23181 | 0.23181 | 60.1777
106 | 630 | 1.4221 | 0.23296 | 0.23296 | 60.4555
107 | 636 | 1.422 | 0.23411 | 0.23411 | 60.7302
108 | 642 | 1.422 | 0.23525 | 0.23525 | 61.002
109 | 648 | 1.4218 | 0.23639 | 0.23639 | 61.2709
110 | 654 | 1.4217 | 0.23752 | 0.23752 | 61.5368
111 | 660 | 1.4215 | 0.23865 | 0.23865 | 61.7997
112 | 666 | 1.4213 | 0.23977 | 0.23977 | 62.0598
113 | 672 | 1.421 | 0.24089 | 0.24089 | 62.3169
114 | 678 | 1.4207 | 0.242 | 0.242 | 62.571
115 | 684 | 1.4204 | 0.24311 | 0.24311 | 62.8223
116 | 690 | 1.42 | 0.24421 | 0.24421 | 63.0706
117 | 696 | 1.4195 | 0.2453 | 0.2453 | 63.316
118 | 702 | 1.419 | 0.24638 | 0.24638 | 63.5585
119 | 708 | 1.4185 | 0.24746 | 0.24746 | 63.798
120 | 714 | 1.4179 | 0.24852 | 0.24852 | 64.0347
121 | 720 | 1.4172 | 0.24958 | 0.24958 | 64.2684
122 | 726 | 1.4165 | 0.25063 | 0.25063 | 64.4991
123 | 732 | 1.4157 | 0.25167 | 0.25167 | 64.727
124 | 738 | 1.4148 | 0.25271 | 0.25271 | 64.9519
125 | 744 | 1.4139 | 0.25373 | 0.25373 | 65.1739
126 | 750 | 1.4129 | 0.25474 | 0.25474 | 65.3929
127 | 756 | 1.4118 | 0.25574 | 0.25574 | 65.6089
128 | 762 | 1.4107 | 0.25673 | 0.25673 | 65.8221
129 | 768 | 1.4095 | 0.2577 | 0.2577 | 66.0322
130 | 774 | 1.4082 | 0.25867 | 0.25867 | 66.2393
131 | 780 | 1.4068 | 0.25962 | 0.25962 | 66.4435
132 | 786 | 1.4054 | 0.26056 | 0.26056 | 66.6447
133 | 792 | 1.4039 | 0.26149 | 0.26149 | 66.8429
134 | 798 | 1.4023 | 0.2624 | 0.2624 | 67.038
135 | 804 | 1.4006 | 0.2633 | 0.2633 | 67.2301
136 | 810 | 1.3988 | 0.26419 | 0.26419 | 67.4192
137 | 816 | 1.3969 | 0.26506 | 0.26506 | 67.6052
138 | 822 | 1.395 | 0.26592 | 0.26592 | 67.7882
139 | 828 | 1.393 | 0.26676 | 0.26676 | 67.9681
140 | 834 | 1.3908 | 0.26758 | 0.26758 | 68.1449
141 | 840 | 1.3886 | 0.26839 | 0.26839 | 68.3186
142 | 846 | 1.3863 | 0.26919 | 0.26919 | 68.4892
143 | 852 | 1.3839 | 0.26996 | 0.26996 | 68.6567
144 | 858 | 1.3814 | 0.27072 | 0.27072 | 68.821
145 | 864 | 1.3788 | 0.27147 | 0.27147 | 68.9822
146 | 870 | 1.3761 | 0.27219 | 0.27219 | 69.1401
147 | 876 | 1.3733 | 0.2729 | 0.2729 | 69.2949
148 | 882 | 1.3704 | 0.27359 | 0.27359 | 69.4465
149 | 888 | 1.3674 | 0.27426 | 0.27426 | 69.5949
150 | 894 | 1.3642 | 0.27492 | 0.27492 | 69.74
151 | 900 | 1.361 | 0.27555 | 0.27555 | 69.8819
152 | 906 | 1.3577 | 0.27617 | 0.27617 | 70.0204
153 | 912 | 1.3543 | 0.27676 | 0.27676 | 70.1557
154 | 918 | 1.3508 | 0.27734 | 0.27734 | 70.2877
155 | 924 | 1.3472 | 0.27789 | 0.27789 | 70.4164
156 | 930 | 1.3435 | 0.27843 | 0.27843 | 70.5417
157 | 936 | 1.3396 | 0.27894 | 0.27894 | 70.6636
158 | 942 | 1.3357 | 0.27944 | 0.27944 | 70.7821
159 | 948 | 1.3316 | 0.27991 | 0.27991 | 70.8972
160 | 954 | 1.3275 | 0.28036 | 0.28036 | 71.0089
161 | 960 | 1.3232 | 0.28079 | 0.28079 | 71.1172
162 | 966 | 1.3189 | 0.2812 | 0.2812 | 71.222
163 | 972 | 1.3144 | 0.28159 | 0.28159 | 71.3232
164 | 978 | 1.3098 | 0.28195 | 0.28195 | 71.421
165 | 984 | 1.3051 | 0.2823 | 0.2823 | 71.5152
166 | 990 | 1.3003 | 0.28261 | 0.28261 | 71.6058
167 | 996 | 1.2954 | 0.28291 | 0.28291 | 71.6929
168 | 1002 | 1.2904 | 0.28319 | 0.28319 | 71.7763
169 | 1008 | 1.2853 | 0.28344 | 0.28344 | 71.8561
170 | 1014 | 1.2801 | 0.28367 | 0.28367 | 71.9322
171 | 1020 | 1.2748 | 0.28387 | 0.28387 | 72.0046
172 | 1026 | 1.2693 | 0.28405 | 0.28405 | 72.0733
173 | 1032 | 1.2638 | 0.28421 | 0.28421 | 72.1382
174 | 1038 | 1.2581 | 0.28434 | 0.28434 | 72.1994
175 | 1044 | 1.2524 | 0.28445 | 0.28445 | 72.2567
176 | 1050 | 1.2465 | 0.28454 | 0.28454 | 72.3102
177 | 1056 | 1.2406 | 0.2846 | 0.2846 | 72.3598
178 | 1062 | 1.2345 | 0.28464 | 0.28464 | 72.4054
179 | 1068 | 1.2283 | 0.28466 | 0.28466 | 72.4472
180 | 1074 | 1.2221 | 0.28465 | 0.28465 | 72.4849
181 | 1080 | 1.2157 | 0.28461 | 0.28461 | 72.5186
182 | 1086 | 1.2092 | 0.28455 | 0.28455 | 72.5482
183 | 1092 | 1.2026 | 0.28447 | 0.28447 | 72.5738
184 | 1098 | 1.196 | 0.28436 | 0.28436 | 72.5951
185 | 1104 | 1.1892 | 0.28423 | 0.28423 | 72.6123
186 | 1110 | 1.1823 | 0.28407 | 0.28407 | 72.6253
187 | 1116 | 1.1754 | 0.28389 | 0.28389 | 72.6339
188 | 1122 | 1.1683 | 0.28368 | 0.28368 | 72.6382
189 | 1128 | 1.1611 | 0.28345 | 0.28345 | 72.6382
190 | 1134 | 1.1539 | 0.2832 | 0.2832 | 72.6337
191 | 1140 | 1.1465 | 0.28292 | 0.28292 | 72.6246
192 | 1146 | 1.1391 | 0.28262 | 0.28262 | 72.6111
193 | 1152 | 1.1316 | 0.28229 | 0.28229 | 72.5929
194 | 1158 | 1.124 | 0.28194 | 0.28194 | 72.57
195 | 1164 | 1.1162 | 0.28156 | 0.28156 | 72.5424
196 | 1170 | 1.1084 | 0.28116 | 0.28116 | 72.51
197 | 1176 | 1.1006 | 0.28074 | 0.28074 | 72.4727
198 | 1182 | 1.0926 | 0.28029 | 0.28029 | 72.4304
199 | 1188 | 1.0845 | 0.27981 | 0.27981 | 72.383
200 | 1194 | 1.0764 | 0.27932 | 0.27932 | 72.3306
201 | 1200 | 1.0681 | 0.2788 | 0.2788 | 72.2729
202 | 1206 | 1.0598 | 0.27825 | 0.27825 | 72.2099
203 | 1212 | 1.0514 | 0.27769 | 0.27769 | 72.1415
204 | 1218 | 1.043 | 0.2771 | 0.2771 | 72.0677
205 | 1224 | 1.0344 | 0.27648 | 0.27648 | 71.9882
206 | 1230 | 1.0258 | 0.27585 | 0.27585 | 71.903
207 | 1236 | 1.0171 | 0.27519 | 0.27519 | 71.812
208 | 1242 | 1.0083 | 0.27451 | 0.27451 | 71.715
209 | 1248 | 0.99944 | 0.2738 | 0.2738 | 71.6119
210 | 1254 | 0.99051 | 0.27308 | 0.27308 | 71.5027
211 | 1260 | 0.98151 | 0.27233 | 0.27233 | 71.3871
212 | 1266 | 0.97243 | 0.27156 | 0.27156 | 71.265
213 | 1272 | 0.96328 | 0.27077 | 0.27077 | 71.1363
214 | 1278 | 0.95406 | 0.26996 | 0.26996 | 71.0008
215 | 1284 | 0.94477 | 0.26913 | 0.26913 | 70.8583
216 | 1290 | 0.93542 | 0.26827 | 0.26827 | 70.7086
217 | 1296 | 0.92599 | 0.2674 | 0.2674 | 70.5517
218 | 1302 | 0.9165 | 0.2665 | 0.2665 | 70.3872
219 | 1308 | 0.90694 | 0.26559 | 0.26559 | 70.215
220 | 1314 | 0.89732 | 0.26466 | 0.26466 | 70.0348
221 | 1320 | 0.88763 | 0.2637 | 0.2637 | 69.8465
222 | 1326 | 0.87788 | 0.26273 | 0.26273 | 69.6499
223 | 1332 | 0.86807 | 0.26174 | 0.26174 | 69.4445
224 | 1338 | 0.85819 | 0.26073 | 0.26073 | 69.2303
225 | 1344 | 0.84825 | 0.25971 | 0.25971 | 69.0069
226 | 1350 | 0.83824 | 0.25866 | 0.25866 | 68.774
227 | 1356 | 0.82818 | 0.2576 | 0.2576 | 68.5314
228 | 1362 | 0.81805 | 0.25652 | 0.25652 | 68.2788
229 | 1368 | 0.80786 | 0.25543 | 0.25543 | 68.0157
230 | 1374 | 0.79761 | 0.25432 | 0.25432 | 67.742
231 | 1380 | 0.7873 | 0.25319 | 0.25319 | 67.4571
232 | 1386 | 0.77693 | 0.25205 | 0.25205 | 67.1608
233 | 1392 | 0.7665 | 0.25089 | 0.25089 | 66.8526
234 | 1398 | 0.756 | 0.24972 | 0.24972 | 66.5321
235 | 1404 | 0.74544 | 0.24853 | 0.24853 | 66.1989
236 | 1410 | 0.73483 | 0.24733 | 0.24733 | 65.8526
237 | 1416 | 0.72414 | 0.24612 | 0.24612 | 65.4926
238 | 1422 | 0.7134 | 0.2449 | 0.2449 | 65.1184
239 | 1428 | 0.70259 | 0.24366 | 0.24366 | 64.7296
240 | 1434 | 0.69172 | 0.24241 | 0.24241 | 64.3256
241 | 1440 | 0.68078 | 0.24115 | 0.24115 | 63.9058
242 | 1446 | 0.66978 | 0.23988 | 0.23988 | 63.4696
243 | 1452 | 0.65871 | 0.23859 | 0.23859 | 63.0163
244 | 1458 | 0.64757 | 0.2373 | 0.2373 | 62.5454
245 | 1464 | 0.63636 | 0.236 | 0.236 | 62.0561
246 | 1470 | 0.62507 | 0.23469 | 0.23469 | 61.5477
247 | 1476 | 0.61372 | 0.23337 | 0.23337 | 61.0194
248 | 1482 | 0.60229 | 0.23204 | 0.23204 | 60.4705
249 | 1488 | 0.59078 | 0.2307 | 0.2307 | 59.9002
250 | 1494 | 0.5792 | 0.22936 | 0.22936 | 59.3075
251 | 1500 | 0.56754 | 0.22801 | 0.22801 | 58.6916
252 | 1506 | 0.55579 | 0.22666 | 0.22666 | 58.0515
253 | 1512 | 0.54395 | 0.2253 | 0.2253 | 57.3862
254 | 1518 | 0.53203 | 0.22393 | 0.22393 | 56.6947
255 | 1524 | 0.52002 | 0.22256 | 0.22256 | 55.976
256 | 1530 | 0.50791 | 0.22119 | 0.22119 | 55.2289
257 | 1536 | 0.49571 | 0.21981 | 0.21981 | 54.4523
258 | 1542 | 0.48341 | 0.21843 | 0.21843 | 53.6448
259 | 1548 | 0.471 | 0.21705 | 0.21705 | 52.8053
260 | 1554 | 0.45849 | 0.21567 | 0.21567 | 51.9325
261 | 1560 | 0.44586 | 0.21429 | 0.21429 | 51.0249
262 | 1566 | 0.43312 | 0.2129 | 0.2129 | 50.081
263 | 1572 | 0.42026 | 0.21152 | 0.21152 | 49.0995
264 | 1578 | 0.40728 | 0.21013 | 0.21013 | 48.0788
265 | 1584 | 0.39416 | 0.20875 | 0.20875 | 47.0172
266 | 1590 | 0.38092 | 0.20737 | 0.20737 | 45.913
267 | 1596 | 0.36753 | 0.20599 | 0.20599 | 44.7645
268 | 1602 | 0.35401 | 0.20462 | 0.20462 | 43.5699
269 | 1608 | 0.34033 | 0.20324 | 0.20324 | 42.3272
270 | 1614 | 0.3265 | 0.20188 | 0.20188 | 41.0346
271 | 1620 | 0.3125 | 0.20051 | 0.20051 | 39.6899
272 | 1626 | 0.29834 | 0.19916 | 0.19916 | 38.2911
273 | 1632 | 0.28401 | 0.1978 | 0.1978 | 36.8359
274 | 1638 | 0.26949 | 0.19646 | 0.19646 | 35.3222
275 | 1644 | 0.25479 | 0.19512 | 0.19512 | 33.7475
276 | 1650 | 0.2399 | 0.19379 | 0.19379 | 32.1094
277 | 1656 | 0.2248 | 0.19247 | 0.19247 | 30.4054
278 | 1662 | 0.20949 | 0.19115 | 0.19115 | 28.6329
279 | 1668 | 0.19396 | 0.18985 | 0.18985 | 26.7893
280 | 1674 | 0.17821 | 0.18855 | 0.18855 | 24.8717
281 | 1680 | 0.16222 | 0.18727 | 0.18727 | 22.8773
282 | 1686 | 0.14599 | 0.186 | 0.186 | 20.8032
283 | 1692 | 0.12951 | 0.18474 | 0.18474 | 18.6464
284 | 1698 | 0.11276 | 0.18349 | 0.18349 | 16.4036
285 | 1704 | 0.095743 | 0.18225 | 0.18225 | 14.0718
286 | 1710 | 0.078441 | 0.18103 | 0.18103 | 11.6476
287 | 1716 | 0.060847 | 0.17983 | 0.17983 | 9.1277
288 | 1722 | 0.042949 | 0.17863 | 0.17863 | 6.5085
289 | 1728 | 0.024737 | 0.17745 | 0.17745 | 3.7866
290 | 1734 | 0.0061981 | 0.17629 | 0.17629 | 0.95836

## 12-100 Curve Tables
Fan Wheel Size 12-100
Operating Curve Data Points
|  |  | 1800 |  | RPM
| CFM | SP | BHP | BHP | Efficiency
|  |  | TOTAL | PER FAN
1 | 0 | 1.4713 | 0.075845 | 0.075845 | 0
2 | 3 | 1.4732 | 0.077042 | 0.077042 | 0.90179
3 | 6 | 1.475 | 0.078224 | 0.078224 | 1.7785
4 | 9 | 1.4768 | 0.079393 | 0.079393 | 2.6317
5 | 12 | 1.4784 | 0.080548 | 0.080548 | 3.4625
6 | 15 | 1.48 | 0.08169 | 0.08169 | 4.2722
7 | 18 | 1.4816 | 0.082818 | 0.082818 | 5.062
8 | 21 | 1.483 | 0.083934 | 0.083934 | 5.8328
9 | 24 | 1.4844 | 0.085037 | 0.085037 | 6.5856
10 | 27 | 1.4857 | 0.086128 | 0.086128 | 7.3214
11 | 30 | 1.4869 | 0.087207 | 0.087207 | 8.0409
12 | 33 | 1.4881 | 0.088273 | 0.088273 | 8.745
13 | 36 | 1.4891 | 0.089328 | 0.089328 | 9.4342
14 | 39 | 1.4902 | 0.090371 | 0.090371 | 10.1094
15 | 42 | 1.4911 | 0.091402 | 0.091402 | 10.7712
16 | 45 | 1.492 | 0.092422 | 0.092422 | 11.4201
17 | 48 | 1.4929 | 0.093431 | 0.093431 | 12.0566
18 | 51 | 1.4936 | 0.094429 | 0.094429 | 12.6813
19 | 54 | 1.4944 | 0.095416 | 0.095416 | 13.2948
20 | 57 | 1.495 | 0.096393 | 0.096393 | 13.8973
21 | 60 | 1.4956 | 0.097359 | 0.097359 | 14.4894
22 | 63 | 1.4962 | 0.098315 | 0.098315 | 15.0715
23 | 66 | 1.4967 | 0.099262 | 0.099262 | 15.6439
24 | 69 | 1.4971 | 0.1002 | 0.1002 | 16.207
25 | 72 | 1.4975 | 0.10112 | 0.10112 | 16.7611
26 | 75 | 1.4979 | 0.10204 | 0.10204 | 17.3065
27 | 78 | 1.4982 | 0.10295 | 0.10295 | 17.8436
28 | 81 | 1.4984 | 0.10385 | 0.10385 | 18.3727
29 | 84 | 1.4986 | 0.10474 | 0.10474 | 18.8939
30 | 87 | 1.4988 | 0.10562 | 0.10562 | 19.4076
31 | 90 | 1.4989 | 0.10649 | 0.10649 | 19.9139
32 | 93 | 1.499 | 0.10735 | 0.10735 | 20.4132
33 | 96 | 1.499 | 0.10821 | 0.10821 | 20.9057
34 | 99 | 1.499 | 0.10906 | 0.10906 | 21.3915
35 | 102 | 1.4989 | 0.10989 | 0.10989 | 21.8708
36 | 105 | 1.4989 | 0.11072 | 0.11072 | 22.3439
37 | 108 | 1.4987 | 0.11155 | 0.11155 | 22.8109
38 | 111 | 1.4986 | 0.11236 | 0.11236 | 23.2719
39 | 114 | 1.4984 | 0.11317 | 0.11317 | 23.7272
40 | 117 | 1.4982 | 0.11397 | 0.11397 | 24.1769
41 | 120 | 1.4979 | 0.11477 | 0.11477 | 24.6211
42 | 123 | 1.4976 | 0.11555 | 0.11555 | 25.0601
43 | 126 | 1.4973 | 0.11633 | 0.11633 | 25.4938
44 | 129 | 1.497 | 0.11711 | 0.11711 | 25.9225
45 | 132 | 1.4966 | 0.11787 | 0.11787 | 26.3463
46 | 135 | 1.4962 | 0.11863 | 0.11863 | 26.7652
47 | 138 | 1.4958 | 0.11939 | 0.11939 | 27.1795
48 | 141 | 1.4953 | 0.12013 | 0.12013 | 27.5892
49 | 144 | 1.4948 | 0.12088 | 0.12088 | 27.9944
50 | 147 | 1.4943 | 0.12161 | 0.12161 | 28.3952
51 | 150 | 1.4938 | 0.12234 | 0.12234 | 28.7917
52 | 153 | 1.4933 | 0.12307 | 0.12307 | 29.184
53 | 156 | 1.4927 | 0.12378 | 0.12378 | 29.5723
54 | 159 | 1.4921 | 0.1245 | 0.1245 | 29.9565
55 | 162 | 1.4915 | 0.12521 | 0.12521 | 30.3367
56 | 165 | 1.4909 | 0.12591 | 0.12591 | 30.7132
57 | 168 | 1.4903 | 0.12661 | 0.12661 | 31.0858
58 | 171 | 1.4896 | 0.1273 | 0.1273 | 31.4547
59 | 174 | 1.4889 | 0.12799 | 0.12799 | 31.82
60 | 177 | 1.4882 | 0.12867 | 0.12867 | 32.1817
61 | 180 | 1.4875 | 0.12935 | 0.12935 | 32.5399
62 | 183 | 1.4868 | 0.13003 | 0.13003 | 32.8947
63 | 186 | 1.4861 | 0.1307 | 0.1307 | 33.2461
64 | 189 | 1.4853 | 0.13136 | 0.13136 | 33.5942
65 | 192 | 1.4846 | 0.13202 | 0.13202 | 33.939
66 | 195 | 1.4838 | 0.13268 | 0.13268 | 34.2807
67 | 198 | 1.483 | 0.13334 | 0.13334 | 34.6191
68 | 201 | 1.4822 | 0.13399 | 0.13399 | 34.9545
69 | 204 | 1.4814 | 0.13463 | 0.13463 | 35.2869
70 | 207 | 1.4806 | 0.13528 | 0.13528 | 35.6162
71 | 210 | 1.4798 | 0.13591 | 0.13591 | 35.9427
72 | 213 | 1.479 | 0.13655 | 0.13655 | 36.2662
73 | 216 | 1.4782 | 0.13718 | 0.13718 | 36.5868
74 | 219 | 1.4773 | 0.13781 | 0.13781 | 36.9047
75 | 222 | 1.4765 | 0.13844 | 0.13844 | 37.2198
76 | 225 | 1.4756 | 0.13906 | 0.13906 | 37.5321
77 | 228 | 1.4748 | 0.13968 | 0.13968 | 37.8418
78 | 231 | 1.4739 | 0.1403 | 0.1403 | 38.1488
79 | 234 | 1.4731 | 0.14092 | 0.14092 | 38.4533
80 | 237 | 1.4722 | 0.14153 | 0.14153 | 38.7551
81 | 240 | 1.4713 | 0.14214 | 0.14214 | 39.0545
82 | 243 | 1.4705 | 0.14274 | 0.14274 | 39.3513
83 | 246 | 1.4696 | 0.14335 | 0.14335 | 39.6457
84 | 249 | 1.4687 | 0.14395 | 0.14395 | 39.9376
85 | 252 | 1.4679 | 0.14455 | 0.14455 | 40.2272
86 | 255 | 1.467 | 0.14515 | 0.14515 | 40.5144
87 | 258 | 1.4661 | 0.14575 | 0.14575 | 40.7993
88 | 261 | 1.4653 | 0.14634 | 0.14634 | 41.0819
89 | 264 | 1.4644 | 0.14693 | 0.14693 | 41.3622
90 | 267 | 1.4635 | 0.14752 | 0.14752 | 41.6403
91 | 270 | 1.4627 | 0.14811 | 0.14811 | 41.9161
92 | 273 | 1.4618 | 0.1487 | 0.1487 | 42.1898
93 | 276 | 1.461 | 0.14928 | 0.14928 | 42.4614
94 | 279 | 1.4601 | 0.14986 | 0.14986 | 42.7308
95 | 282 | 1.4592 | 0.15045 | 0.15045 | 42.9981
96 | 285 | 1.4584 | 0.15103 | 0.15103 | 43.2634
97 | 288 | 1.4575 | 0.15161 | 0.15161 | 43.5266
98 | 291 | 1.4567 | 0.15218 | 0.15218 | 43.7878
99 | 294 | 1.4559 | 0.15276 | 0.15276 | 44.047
100 | 297 | 1.455 | 0.15333 | 0.15333 | 44.3042
101 | 300 | 1.4542 | 0.15391 | 0.15391 | 44.5595
102 | 303 | 1.4534 | 0.15448 | 0.15448 | 44.8129
103 | 306 | 1.4526 | 0.15505 | 0.15505 | 45.0643
104 | 309 | 1.4518 | 0.15562 | 0.15562 | 45.3139
105 | 312 | 1.451 | 0.15619 | 0.15619 | 45.5617
106 | 315 | 1.4502 | 0.15676 | 0.15676 | 45.8076
107 | 318 | 1.4494 | 0.15733 | 0.15733 | 46.0517
108 | 321 | 1.4486 | 0.1579 | 0.1579 | 46.294
109 | 324 | 1.4478 | 0.15847 | 0.15847 | 46.5345
110 | 327 | 1.4471 | 0.15903 | 0.15903 | 46.7733
111 | 330 | 1.4463 | 0.1596 | 0.1596 | 47.0104
112 | 333 | 1.4455 | 0.16016 | 0.16016 | 47.2458
113 | 336 | 1.4448 | 0.16073 | 0.16073 | 47.4795
114 | 339 | 1.4441 | 0.16129 | 0.16129 | 47.7115
115 | 342 | 1.4433 | 0.16186 | 0.16186 | 47.9418
116 | 345 | 1.4426 | 0.16242 | 0.16242 | 48.1706
117 | 348 | 1.4419 | 0.16298 | 0.16298 | 48.3977
118 | 351 | 1.4412 | 0.16355 | 0.16355 | 48.6232
119 | 354 | 1.4405 | 0.16411 | 0.16411 | 48.8472
120 | 357 | 1.4398 | 0.16467 | 0.16467 | 49.0696
121 | 360 | 1.4391 | 0.16523 | 0.16523 | 49.2904
122 | 363 | 1.4385 | 0.16579 | 0.16579 | 49.5098
123 | 366 | 1.4378 | 0.16636 | 0.16636 | 49.7276
124 | 369 | 1.4372 | 0.16692 | 0.16692 | 49.944
125 | 372 | 1.4365 | 0.16748 | 0.16748 | 50.1588
126 | 375 | 1.4359 | 0.16804 | 0.16804 | 50.3722
127 | 378 | 1.4353 | 0.1686 | 0.1686 | 50.5842
128 | 381 | 1.4347 | 0.16916 | 0.16916 | 50.7948
129 | 384 | 1.4341 | 0.16973 | 0.16973 | 51.0039
130 | 387 | 1.4335 | 0.17029 | 0.17029 | 51.2116
131 | 390 | 1.4329 | 0.17085 | 0.17085 | 51.418
132 | 393 | 1.4323 | 0.17141 | 0.17141 | 51.623
133 | 396 | 1.4318 | 0.17197 | 0.17197 | 51.8266
134 | 399 | 1.4312 | 0.17254 | 0.17254 | 52.029
135 | 402 | 1.4307 | 0.1731 | 0.1731 | 52.2299
136 | 405 | 1.4301 | 0.17366 | 0.17366 | 52.4296
137 | 408 | 1.4296 | 0.17423 | 0.17423 | 52.628
138 | 411 | 1.4291 | 0.17479 | 0.17479 | 52.8251
139 | 414 | 1.4286 | 0.17535 | 0.17535 | 53.021
140 | 417 | 1.4281 | 0.17592 | 0.17592 | 53.2155
141 | 420 | 1.4276 | 0.17648 | 0.17648 | 53.4089
142 | 423 | 1.4271 | 0.17705 | 0.17705 | 53.601
143 | 426 | 1.4267 | 0.17761 | 0.17761 | 53.7919
144 | 429 | 1.4262 | 0.17818 | 0.17818 | 53.9816
145 | 432 | 1.4258 | 0.17874 | 0.17874 | 54.1701
146 | 435 | 1.4253 | 0.17931 | 0.17931 | 54.3574
147 | 438 | 1.4249 | 0.17988 | 0.17988 | 54.5436
148 | 441 | 1.4245 | 0.18044 | 0.18044 | 54.7286
149 | 444 | 1.4241 | 0.18101 | 0.18101 | 54.9124
150 | 447 | 1.4237 | 0.18158 | 0.18158 | 55.0952
151 | 450 | 1.4233 | 0.18215 | 0.18215 | 55.2768
152 | 453 | 1.4229 | 0.18272 | 0.18272 | 55.4573
153 | 456 | 1.4226 | 0.18328 | 0.18328 | 55.6367
154 | 459 | 1.4222 | 0.18385 | 0.18385 | 55.815
155 | 462 | 1.4218 | 0.18442 | 0.18442 | 55.9922
156 | 465 | 1.4215 | 0.18499 | 0.18499 | 56.1683
157 | 468 | 1.4212 | 0.18557 | 0.18557 | 56.3434
158 | 471 | 1.4208 | 0.18614 | 0.18614 | 56.5174
159 | 474 | 1.4205 | 0.18671 | 0.18671 | 56.6904
160 | 477 | 1.4202 | 0.18728 | 0.18728 | 56.8624
161 | 480 | 1.4199 | 0.18785 | 0.18785 | 57.0334
162 | 483 | 1.4196 | 0.18843 | 0.18843 | 57.2033
163 | 486 | 1.4193 | 0.189 | 0.189 | 57.3722
164 | 489 | 1.419 | 0.18958 | 0.18958 | 57.5401
165 | 492 | 1.4188 | 0.19015 | 0.19015 | 57.7071
166 | 495 | 1.4185 | 0.19072 | 0.19072 | 57.8731
167 | 498 | 1.4182 | 0.1913 | 0.1913 | 58.0381
168 | 501 | 1.418 | 0.19188 | 0.19188 | 58.2021
169 | 504 | 1.4177 | 0.19245 | 0.19245 | 58.3652
170 | 507 | 1.4175 | 0.19303 | 0.19303 | 58.5273
171 | 510 | 1.4173 | 0.19361 | 0.19361 | 58.6885
172 | 513 | 1.417 | 0.19418 | 0.19418 | 58.8488
173 | 516 | 1.4168 | 0.19476 | 0.19476 | 59.0081
174 | 519 | 1.4166 | 0.19534 | 0.19534 | 59.1666
175 | 522 | 1.4164 | 0.19592 | 0.19592 | 59.3241
176 | 525 | 1.4162 | 0.1965 | 0.1965 | 59.4807
177 | 528 | 1.416 | 0.19708 | 0.19708 | 59.6364
178 | 531 | 1.4158 | 0.19766 | 0.19766 | 59.7912
179 | 534 | 1.4156 | 0.19824 | 0.19824 | 59.9452
180 | 537 | 1.4154 | 0.19882 | 0.19882 | 60.0982
181 | 540 | 1.4152 | 0.1994 | 0.1994 | 60.2504
182 | 543 | 1.4151 | 0.19998 | 0.19998 | 60.4018
183 | 546 | 1.4149 | 0.20056 | 0.20056 | 60.5523
184 | 549 | 1.4147 | 0.20114 | 0.20114 | 60.7019
185 | 552 | 1.4146 | 0.20172 | 0.20172 | 60.8506
186 | 555 | 1.4144 | 0.2023 | 0.2023 | 60.9986
187 | 558 | 1.4142 | 0.20288 | 0.20288 | 61.1457
188 | 561 | 1.4141 | 0.20346 | 0.20346 | 61.2919
189 | 564 | 1.4139 | 0.20405 | 0.20405 | 61.4373
190 | 567 | 1.4138 | 0.20463 | 0.20463 | 61.5819
191 | 570 | 1.4136 | 0.20521 | 0.20521 | 61.7257
192 | 573 | 1.4135 | 0.20579 | 0.20579 | 61.8687
193 | 576 | 1.4133 | 0.20637 | 0.20637 | 62.0108
194 | 579 | 1.4132 | 0.20695 | 0.20695 | 62.1522
195 | 582 | 1.413 | 0.20754 | 0.20754 | 62.2927
196 | 585 | 1.4129 | 0.20812 | 0.20812 | 62.4325
197 | 588 | 1.4128 | 0.2087 | 0.2087 | 62.5715
198 | 591 | 1.4126 | 0.20928 | 0.20928 | 62.7096
199 | 594 | 1.4125 | 0.20986 | 0.20986 | 62.847
200 | 597 | 1.4123 | 0.21044 | 0.21044 | 62.9836
201 | 600 | 1.4122 | 0.21102 | 0.21102 | 63.1194
202 | 603 | 1.412 | 0.2116 | 0.2116 | 63.2544
203 | 606 | 1.4119 | 0.21218 | 0.21218 | 63.3887
204 | 609 | 1.4117 | 0.21276 | 0.21276 | 63.5221
205 | 612 | 1.4116 | 0.21334 | 0.21334 | 63.6548
206 | 615 | 1.4114 | 0.21392 | 0.21392 | 63.7868
207 | 618 | 1.4113 | 0.2145 | 0.2145 | 63.918
208 | 621 | 1.4111 | 0.21508 | 0.21508 | 64.0484
209 | 624 | 1.411 | 0.21566 | 0.21566 | 64.178
210 | 627 | 1.4108 | 0.21624 | 0.21624 | 64.3069
211 | 630 | 1.4106 | 0.21681 | 0.21681 | 64.435
212 | 633 | 1.4105 | 0.21739 | 0.21739 | 64.5624
213 | 636 | 1.4103 | 0.21796 | 0.21796 | 64.689
214 | 639 | 1.4101 | 0.21854 | 0.21854 | 64.8149
215 | 642 | 1.4099 | 0.21911 | 0.21911 | 64.94
216 | 645 | 1.4097 | 0.21969 | 0.21969 | 65.0643
217 | 648 | 1.4095 | 0.22026 | 0.22026 | 65.1879
218 | 651 | 1.4093 | 0.22083 | 0.22083 | 65.3108
219 | 654 | 1.4091 | 0.2214 | 0.2214 | 65.4329
220 | 657 | 1.4089 | 0.22197 | 0.22197 | 65.5543
221 | 660 | 1.4087 | 0.22254 | 0.22254 | 65.6749
222 | 663 | 1.4085 | 0.22311 | 0.22311 | 65.7947
223 | 666 | 1.4082 | 0.22368 | 0.22368 | 65.9139
224 | 669 | 1.408 | 0.22425 | 0.22425 | 66.0322
225 | 672 | 1.4077 | 0.22481 | 0.22481 | 66.1499
226 | 675 | 1.4075 | 0.22538 | 0.22538 | 66.2667
227 | 678 | 1.4072 | 0.22594 | 0.22594 | 66.3829
228 | 681 | 1.407 | 0.2265 | 0.2265 | 66.4983
229 | 684 | 1.4067 | 0.22706 | 0.22706 | 66.6129
230 | 687 | 1.4064 | 0.22762 | 0.22762 | 66.7268
231 | 690 | 1.4061 | 0.22818 | 0.22818 | 66.8399
232 | 693 | 1.4058 | 0.22874 | 0.22874 | 66.9523
233 | 696 | 1.4054 | 0.22929 | 0.22929 | 67.064
234 | 699 | 1.4051 | 0.22984 | 0.22984 | 67.1749
235 | 702 | 1.4048 | 0.2304 | 0.2304 | 67.285
236 | 705 | 1.4044 | 0.23095 | 0.23095 | 67.3944
237 | 708 | 1.404 | 0.2315 | 0.2315 | 67.503
238 | 711 | 1.4037 | 0.23204 | 0.23204 | 67.6109
239 | 714 | 1.4033 | 0.23259 | 0.23259 | 67.718
240 | 717 | 1.4029 | 0.23313 | 0.23313 | 67.8244
241 | 720 | 1.4025 | 0.23368 | 0.23368 | 67.93
242 | 723 | 1.402 | 0.23422 | 0.23422 | 68.0349
243 | 726 | 1.4016 | 0.23476 | 0.23476 | 68.1389
244 | 729 | 1.4011 | 0.23529 | 0.23529 | 68.2423
245 | 732 | 1.4007 | 0.23583 | 0.23583 | 68.3448
246 | 735 | 1.4002 | 0.23636 | 0.23636 | 68.4466
247 | 738 | 1.3997 | 0.23689 | 0.23689 | 68.5476
248 | 741 | 1.3992 | 0.23742 | 0.23742 | 68.6478
249 | 744 | 1.3986 | 0.23795 | 0.23795 | 68.7473
250 | 747 | 1.3981 | 0.23847 | 0.23847 | 68.846
251 | 750 | 1.3975 | 0.23899 | 0.23899 | 68.9439
252 | 753 | 1.397 | 0.23951 | 0.23951 | 69.041
253 | 756 | 1.3964 | 0.24003 | 0.24003 | 69.1373
254 | 759 | 1.3958 | 0.24054 | 0.24054 | 69.2329
255 | 762 | 1.3951 | 0.24106 | 0.24106 | 69.3276
256 | 765 | 1.3945 | 0.24157 | 0.24157 | 69.4215
257 | 768 | 1.3938 | 0.24207 | 0.24207 | 69.5147
258 | 771 | 1.3932 | 0.24258 | 0.24258 | 69.607
259 | 774 | 1.3925 | 0.24308 | 0.24308 | 69.6986
260 | 777 | 1.3917 | 0.24358 | 0.24358 | 69.7893
261 | 780 | 1.391 | 0.24408 | 0.24408 | 69.8792
262 | 783 | 1.3903 | 0.24457 | 0.24457 | 69.9683
263 | 786 | 1.3895 | 0.24506 | 0.24506 | 70.0566
264 | 789 | 1.3887 | 0.24555 | 0.24555 | 70.1441
265 | 792 | 1.3879 | 0.24604 | 0.24604 | 70.2307
266 | 795 | 1.387 | 0.24652 | 0.24652 | 70.3165
267 | 798 | 1.3862 | 0.247 | 0.247 | 70.4015
268 | 801 | 1.3853 | 0.24748 | 0.24748 | 70.4856
269 | 804 | 1.3844 | 0.24795 | 0.24795 | 70.5689
270 | 807 | 1.3835 | 0.24842 | 0.24842 | 70.6514
271 | 810 | 1.3826 | 0.24889 | 0.24889 | 70.7329
272 | 813 | 1.3816 | 0.24935 | 0.24935 | 70.8137
273 | 816 | 1.3806 | 0.24981 | 0.24981 | 70.8935
274 | 819 | 1.3796 | 0.25027 | 0.25027 | 70.9725
275 | 822 | 1.3786 | 0.25072 | 0.25072 | 71.0507
276 | 825 | 1.3775 | 0.25117 | 0.25117 | 71.1279
277 | 828 | 1.3764 | 0.25161 | 0.25161 | 71.2043
278 | 831 | 1.3753 | 0.25206 | 0.25206 | 71.2798
279 | 834 | 1.3742 | 0.2525 | 0.2525 | 71.3544
280 | 837 | 1.3731 | 0.25293 | 0.25293 | 71.4281
281 | 840 | 1.3719 | 0.25336 | 0.25336 | 71.5009
282 | 843 | 1.3707 | 0.25379 | 0.25379 | 71.5728
283 | 846 | 1.3695 | 0.25421 | 0.25421 | 71.6438
284 | 849 | 1.3682 | 0.25463 | 0.25463 | 71.7139
285 | 852 | 1.3669 | 0.25505 | 0.25505 | 71.783
286 | 855 | 1.3656 | 0.25546 | 0.25546 | 71.8512
287 | 858 | 1.3643 | 0.25587 | 0.25587 | 71.9185
288 | 861 | 1.363 | 0.25627 | 0.25627 | 71.9848
289 | 864 | 1.3616 | 0.25667 | 0.25667 | 72.0502
290 | 867 | 1.3602 | 0.25706 | 0.25706 | 72.1147
291 | 870 | 1.3587 | 0.25745 | 0.25745 | 72.1782
292 | 873 | 1.3573 | 0.25784 | 0.25784 | 72.2407
293 | 876 | 1.3558 | 0.25822 | 0.25822 | 72.3023
294 | 879 | 1.3543 | 0.2586 | 0.2586 | 72.3628
295 | 882 | 1.3527 | 0.25897 | 0.25897 | 72.4224
296 | 885 | 1.3511 | 0.25934 | 0.25934 | 72.481
297 | 888 | 1.3495 | 0.25971 | 0.25971 | 72.5386
298 | 891 | 1.3479 | 0.26006 | 0.26006 | 72.5953
299 | 894 | 1.3462 | 0.26042 | 0.26042 | 72.6509
300 | 897 | 1.3446 | 0.26077 | 0.26077 | 72.7054
301 | 900 | 1.3428 | 0.26111 | 0.26111 | 72.759
302 | 903 | 1.3411 | 0.26145 | 0.26145 | 72.8115
303 | 906 | 1.3393 | 0.26179 | 0.26179 | 72.863
304 | 909 | 1.3375 | 0.26212 | 0.26212 | 72.9135
305 | 912 | 1.3356 | 0.26244 | 0.26244 | 72.9628
306 | 915 | 1.3338 | 0.26276 | 0.26276 | 73.0112
307 | 918 | 1.3319 | 0.26308 | 0.26308 | 73.0584
308 | 921 | 1.3299 | 0.26339 | 0.26339 | 73.1046
309 | 924 | 1.328 | 0.26369 | 0.26369 | 73.1497
310 | 927 | 1.326 | 0.26399 | 0.26399 | 73.1938
311 | 930 | 1.3239 | 0.26429 | 0.26429 | 73.2367
312 | 933 | 1.3219 | 0.26458 | 0.26458 | 73.2785
313 | 936 | 1.3198 | 0.26486 | 0.26486 | 73.3192
314 | 939 | 1.3177 | 0.26514 | 0.26514 | 73.3588
315 | 942 | 1.3155 | 0.26541 | 0.26541 | 73.3972
316 | 945 | 1.3133 | 0.26568 | 0.26568 | 73.4345
317 | 948 | 1.3111 | 0.26594 | 0.26594 | 73.4707
318 | 951 | 1.3088 | 0.26619 | 0.26619 | 73.5057
319 | 954 | 1.3066 | 0.26644 | 0.26644 | 73.5395
320 | 957 | 1.3042 | 0.26669 | 0.26669 | 73.5722
321 | 960 | 1.3019 | 0.26693 | 0.26693 | 73.6037
322 | 963 | 1.2995 | 0.26716 | 0.26716 | 73.6339
323 | 966 | 1.2971 | 0.26739 | 0.26739 | 73.663
324 | 969 | 1.2946 | 0.26761 | 0.26761 | 73.6909
325 | 972 | 1.2921 | 0.26782 | 0.26782 | 73.7176
326 | 975 | 1.2896 | 0.26803 | 0.26803 | 73.743
327 | 978 | 1.287 | 0.26823 | 0.26823 | 73.7672
328 | 981 | 1.2844 | 0.26843 | 0.26843 | 73.7901
329 | 984 | 1.2818 | 0.26862 | 0.26862 | 73.8118
330 | 987 | 1.2791 | 0.2688 | 0.2688 | 73.8322
331 | 990 | 1.2764 | 0.26898 | 0.26898 | 73.8513
332 | 993 | 1.2737 | 0.26915 | 0.26915 | 73.8692
333 | 996 | 1.2709 | 0.26932 | 0.26932 | 73.8857
334 | 999 | 1.2681 | 0.26948 | 0.26948 | 73.901
335 | 1002 | 1.2653 | 0.26963 | 0.26963 | 73.9149
336 | 1005 | 1.2624 | 0.26978 | 0.26978 | 73.9275
337 | 1008 | 1.2595 | 0.26992 | 0.26992 | 73.9387
338 | 1011 | 1.2565 | 0.27005 | 0.27005 | 73.9486
339 | 1014 | 1.2535 | 0.27018 | 0.27018 | 73.9571
340 | 1017 | 1.2505 | 0.2703 | 0.2703 | 73.9643
341 | 1020 | 1.2475 | 0.27041 | 0.27041 | 73.9701
342 | 1023 | 1.2444 | 0.27052 | 0.27052 | 73.9744
343 | 1026 | 1.2412 | 0.27062 | 0.27062 | 73.9774
344 | 1029 | 1.2381 | 0.27071 | 0.27071 | 73.9789
345 | 1032 | 1.2349 | 0.2708 | 0.2708 | 73.9791
346 | 1035 | 1.2316 | 0.27088 | 0.27088 | 73.9777
347 | 1038 | 1.2283 | 0.27095 | 0.27095 | 73.9749
348 | 1041 | 1.225 | 0.27101 | 0.27101 | 73.9707
349 | 1044 | 1.2217 | 0.27107 | 0.27107 | 73.9649
350 | 1047 | 1.2183 | 0.27112 | 0.27112 | 73.9577
351 | 1050 | 1.2149 | 0.27117 | 0.27117 | 73.9489
352 | 1053 | 1.2114 | 0.27121 | 0.27121 | 73.9387
353 | 1056 | 1.2079 | 0.27124 | 0.27124 | 73.9269
354 | 1059 | 1.2044 | 0.27126 | 0.27126 | 73.9135
355 | 1062 | 1.2008 | 0.27127 | 0.27127 | 73.8986
356 | 1065 | 1.1972 | 0.27128 | 0.27128 | 73.8821
357 | 1068 | 1.1935 | 0.27129 | 0.27129 | 73.864
358 | 1071 | 1.1898 | 0.27128 | 0.27128 | 73.8444
359 | 1074 | 1.1861 | 0.27127 | 0.27127 | 73.8231
360 | 1077 | 1.1824 | 0.27125 | 0.27125 | 73.8002
361 | 1080 | 1.1786 | 0.27122 | 0.27122 | 73.7756
362 | 1083 | 1.1747 | 0.27118 | 0.27118 | 73.7494
363 | 1086 | 1.1709 | 0.27114 | 0.27114 | 73.7214
364 | 1089 | 1.167 | 0.27109 | 0.27109 | 73.6919
365 | 1092 | 1.163 | 0.27103 | 0.27103 | 73.6606
366 | 1095 | 1.159 | 0.27097 | 0.27097 | 73.6275
367 | 1098 | 1.155 | 0.27089 | 0.27089 | 73.5928
368 | 1101 | 1.1509 | 0.27081 | 0.27081 | 73.5563
369 | 1104 | 1.1468 | 0.27073 | 0.27073 | 73.518
370 | 1107 | 1.1427 | 0.27063 | 0.27063 | 73.4779
371 | 1110 | 1.1385 | 0.27053 | 0.27053 | 73.4361
372 | 1113 | 1.1343 | 0.27042 | 0.27042 | 73.3924
373 | 1116 | 1.1301 | 0.2703 | 0.2703 | 73.3468
374 | 1119 | 1.1258 | 0.27017 | 0.27017 | 73.2995
375 | 1122 | 1.1215 | 0.27004 | 0.27004 | 73.2502
376 | 1125 | 1.1171 | 0.2699 | 0.2699 | 73.1991
377 | 1128 | 1.1127 | 0.26975 | 0.26975 | 73.146
378 | 1131 | 1.1083 | 0.26959 | 0.26959 | 73.0911
379 | 1134 | 1.1038 | 0.26942 | 0.26942 | 73.0342
380 | 1137 | 1.0993 | 0.26925 | 0.26925 | 72.9753
381 | 1140 | 1.0948 | 0.26907 | 0.26907 | 72.9144
382 | 1143 | 1.0902 | 0.26888 | 0.26888 | 72.8516
383 | 1146 | 1.0856 | 0.26868 | 0.26868 | 72.7867
384 | 1149 | 1.0809 | 0.26848 | 0.26848 | 72.7198
385 | 1152 | 1.0762 | 0.26827 | 0.26827 | 72.6508
386 | 1155 | 1.0715 | 0.26804 | 0.26804 | 72.5798
387 | 1158 | 1.0667 | 0.26782 | 0.26782 | 72.5066
388 | 1161 | 1.0619 | 0.26758 | 0.26758 | 72.4313
389 | 1164 | 1.0571 | 0.26733 | 0.26733 | 72.3539
390 | 1167 | 1.0522 | 0.26708 | 0.26708 | 72.2743
391 | 1170 | 1.0473 | 0.26682 | 0.26682 | 72.1926
392 | 1173 | 1.0424 | 0.26655 | 0.26655 | 72.1086
393 | 1176 | 1.0374 | 0.26627 | 0.26627 | 72.0224
394 | 1179 | 1.0324 | 0.26599 | 0.26599 | 71.9339
395 | 1182 | 1.0273 | 0.2657 | 0.2657 | 71.8432
396 | 1185 | 1.0222 | 0.26539 | 0.26539 | 71.7502
397 | 1188 | 1.0171 | 0.26509 | 0.26509 | 71.6548
398 | 1191 | 1.0119 | 0.26477 | 0.26477 | 71.5571
399 | 1194 | 1.0067 | 0.26444 | 0.26444 | 71.457
400 | 1197 | 1.0015 | 0.26411 | 0.26411 | 71.3545
401 | 1200 | 0.99625 | 0.26377 | 0.26377 | 71.2496
402 | 1203 | 0.99095 | 0.26342 | 0.26342 | 71.1423
403 | 1206 | 0.98562 | 0.26306 | 0.26306 | 71.0325
404 | 1209 | 0.98025 | 0.26269 | 0.26269 | 70.9201
405 | 1212 | 0.97485 | 0.26232 | 0.26232 | 70.8053
406 | 1215 | 0.96942 | 0.26194 | 0.26194 | 70.6879
407 | 1218 | 0.96395 | 0.26155 | 0.26155 | 70.5679
408 | 1221 | 0.95845 | 0.26115 | 0.26115 | 70.4453
409 | 1224 | 0.95291 | 0.26074 | 0.26074 | 70.3201
410 | 1227 | 0.94734 | 0.26032 | 0.26032 | 70.1922
411 | 1230 | 0.94174 | 0.2599 | 0.2599 | 70.0616
412 | 1233 | 0.9361 | 0.25947 | 0.25947 | 69.9282
413 | 1236 | 0.93044 | 0.25903 | 0.25903 | 69.7922
414 | 1239 | 0.92474 | 0.25858 | 0.25858 | 69.6533
415 | 1242 | 0.919 | 0.25813 | 0.25813 | 69.5116
416 | 1245 | 0.91324 | 0.25766 | 0.25766 | 69.3671
417 | 1248 | 0.90744 | 0.25719 | 0.25719 | 69.2197
418 | 1251 | 0.90162 | 0.25671 | 0.25671 | 69.0694
419 | 1254 | 0.89576 | 0.25622 | 0.25622 | 68.9161
420 | 1257 | 0.88987 | 0.25573 | 0.25573 | 68.7598
421 | 1260 | 0.88395 | 0.25522 | 0.25522 | 68.6006
422 | 1263 | 0.878 | 0.25471 | 0.25471 | 68.4383
423 | 1266 | 0.87202 | 0.25419 | 0.25419 | 68.2729
424 | 1269 | 0.866 | 0.25366 | 0.25366 | 68.1044
425 | 1272 | 0.85996 | 0.25313 | 0.25313 | 67.9327
426 | 1275 | 0.85389 | 0.25258 | 0.25258 | 67.7578
427 | 1278 | 0.84779 | 0.25203 | 0.25203 | 67.5798
428 | 1281 | 0.84166 | 0.25147 | 0.25147 | 67.3984
429 | 1284 | 0.83551 | 0.2509 | 0.2509 | 67.2138
430 | 1287 | 0.82932 | 0.25033 | 0.25033 | 67.0258
431 | 1290 | 0.8231 | 0.24975 | 0.24975 | 66.8344
432 | 1293 | 0.81686 | 0.24915 | 0.24915 | 66.6396
433 | 1296 | 0.81059 | 0.24855 | 0.24855 | 66.4413
434 | 1299 | 0.8043 | 0.24795 | 0.24795 | 66.2395
435 | 1302 | 0.79797 | 0.24733 | 0.24733 | 66.0342
436 | 1305 | 0.79162 | 0.24671 | 0.24671 | 65.8253
437 | 1308 | 0.78524 | 0.24608 | 0.24608 | 65.6127
438 | 1311 | 0.77884 | 0.24544 | 0.24544 | 65.3965
439 | 1314 | 0.77241 | 0.2448 | 0.2448 | 65.1766
440 | 1317 | 0.76596 | 0.24414 | 0.24414 | 64.9528
441 | 1320 | 0.75948 | 0.24348 | 0.24348 | 64.7253
442 | 1323 | 0.75298 | 0.24281 | 0.24281 | 64.4939
443 | 1326 | 0.74645 | 0.24214 | 0.24214 | 64.2586
444 | 1329 | 0.7399 | 0.24146 | 0.24146 | 64.0193
445 | 1332 | 0.73332 | 0.24076 | 0.24076 | 63.776
446 | 1335 | 0.72672 | 0.24007 | 0.24007 | 63.5287
447 | 1338 | 0.7201 | 0.23936 | 0.23936 | 63.2772
448 | 1341 | 0.71346 | 0.23865 | 0.23865 | 63.0216
449 | 1344 | 0.70679 | 0.23793 | 0.23793 | 62.7618
450 | 1347 | 0.7001 | 0.2372 | 0.2372 | 62.4977
451 | 1350 | 0.69339 | 0.23647 | 0.23647 | 62.2293
452 | 1353 | 0.68666 | 0.23572 | 0.23572 | 61.9565
453 | 1356 | 0.67991 | 0.23498 | 0.23498 | 61.6793
454 | 1359 | 0.67314 | 0.23422 | 0.23422 | 61.3976
455 | 1362 | 0.66634 | 0.23346 | 0.23346 | 61.1113
456 | 1365 | 0.65953 | 0.23269 | 0.23269 | 60.8204
457 | 1368 | 0.6527 | 0.23191 | 0.23191 | 60.5249
458 | 1371 | 0.64585 | 0.23113 | 0.23113 | 60.2246
459 | 1374 | 0.63899 | 0.23034 | 0.23034 | 59.9196
460 | 1377 | 0.6321 | 0.22954 | 0.22954 | 59.6097
461 | 1380 | 0.6252 | 0.22873 | 0.22873 | 59.2948
462 | 1383 | 0.61828 | 0.22792 | 0.22792 | 58.975
463 | 1386 | 0.61134 | 0.22711 | 0.22711 | 58.6502
464 | 1389 | 0.60439 | 0.22628 | 0.22628 | 58.3202
465 | 1392 | 0.59742 | 0.22545 | 0.22545 | 57.9851
466 | 1395 | 0.59044 | 0.22462 | 0.22462 | 57.6447
467 | 1398 | 0.58344 | 0.22377 | 0.22377 | 57.299
468 | 1401 | 0.57643 | 0.22292 | 0.22292 | 56.9479
469 | 1404 | 0.5694 | 0.22207 | 0.22207 | 56.5913
470 | 1407 | 0.56236 | 0.22121 | 0.22121 | 56.2292
471 | 1410 | 0.55531 | 0.22034 | 0.22034 | 55.8615
472 | 1413 | 0.54824 | 0.21947 | 0.21947 | 55.4881
473 | 1416 | 0.54116 | 0.21859 | 0.21859 | 55.109
474 | 1419 | 0.53408 | 0.2177 | 0.2177 | 54.724
475 | 1422 | 0.52698 | 0.21681 | 0.21681 | 54.3331
476 | 1425 | 0.51986 | 0.21591 | 0.21591 | 53.9362
477 | 1428 | 0.51274 | 0.21501 | 0.21501 | 53.5332
478 | 1431 | 0.50561 | 0.2141 | 0.2141 | 53.124
479 | 1434 | 0.49847 | 0.21319 | 0.21319 | 52.7086
480 | 1437 | 0.49132 | 0.21227 | 0.21227 | 52.2868
481 | 1440 | 0.48417 | 0.21134 | 0.21134 | 51.8587
482 | 1443 | 0.477 | 0.21041 | 0.21041 | 51.424
483 | 1446 | 0.46983 | 0.20948 | 0.20948 | 50.9827
484 | 1449 | 0.46266 | 0.20854 | 0.20854 | 50.5348
485 | 1452 | 0.45547 | 0.20759 | 0.20759 | 50.0801
486 | 1455 | 0.44828 | 0.20664 | 0.20664 | 49.6184
487 | 1458 | 0.44109 | 0.20569 | 0.20569 | 49.1499
488 | 1461 | 0.43389 | 0.20473 | 0.20473 | 48.6742
489 | 1464 | 0.42669 | 0.20377 | 0.20377 | 48.1914
490 | 1467 | 0.41948 | 0.2028 | 0.2028 | 47.7014
491 | 1470 | 0.41227 | 0.20182 | 0.20182 | 47.204
492 | 1473 | 0.40506 | 0.20085 | 0.20085 | 46.6991
493 | 1476 | 0.39785 | 0.19987 | 0.19987 | 46.1866
494 | 1479 | 0.39063 | 0.19888 | 0.19888 | 45.6665
495 | 1482 | 0.38342 | 0.19789 | 0.19789 | 45.1387
496 | 1485 | 0.3762 | 0.1969 | 0.1969 | 44.6029
497 | 1488 | 0.36899 | 0.1959 | 0.1959 | 44.0592
498 | 1491 | 0.36177 | 0.1949 | 0.1949 | 43.5073
499 | 1494 | 0.35456 | 0.19389 | 0.19389 | 42.9473
500 | 1497 | 0.34735 | 0.19288 | 0.19288 | 42.3789
501 | 1500 | 0.34014 | 0.19187 | 0.19187 | 41.8022
502 | 1503 | 0.33294 | 0.19085 | 0.19085 | 41.2168
503 | 1506 | 0.32574 | 0.18984 | 0.18984 | 40.6228
504 | 1509 | 0.31854 | 0.18881 | 0.18881 | 40.0201
505 | 1512 | 0.31135 | 0.18779 | 0.18779 | 39.4084
506 | 1515 | 0.30417 | 0.18676 | 0.18676 | 38.7877
507 | 1518 | 0.29699 | 0.18573 | 0.18573 | 38.1579
508 | 1521 | 0.28982 | 0.1847 | 0.1847 | 37.5188
509 | 1524 | 0.28266 | 0.18366 | 0.18366 | 36.8703
510 | 1527 | 0.2755 | 0.18262 | 0.18262 | 36.2123
511 | 1530 | 0.26835 | 0.18158 | 0.18158 | 35.5447
512 | 1533 | 0.26122 | 0.18054 | 0.18054 | 34.8673
513 | 1536 | 0.25409 | 0.1795 | 0.1795 | 34.1801
514 | 1539 | 0.24697 | 0.17845 | 0.17845 | 33.4828
515 | 1542 | 0.23987 | 0.1774 | 0.1774 | 32.7754
516 | 1545 | 0.23277 | 0.17635 | 0.17635 | 32.0577
517 | 1548 | 0.22569 | 0.1753 | 0.1753 | 31.3296
518 | 1551 | 0.21863 | 0.17425 | 0.17425 | 30.591
519 | 1554 | 0.21157 | 0.1732 | 0.1732 | 29.8417
520 | 1557 | 0.20453 | 0.17214 | 0.17214 | 29.0816
521 | 1560 | 0.19751 | 0.17109 | 0.17109 | 28.3106
522 | 1563 | 0.1905 | 0.17003 | 0.17003 | 27.5285
523 | 1566 | 0.18351 | 0.16897 | 0.16897 | 26.7353
524 | 1569 | 0.17653 | 0.16791 | 0.16791 | 25.9307
525 | 1572 | 0.16957 | 0.16686 | 0.16686 | 25.1146
526 | 1575 | 0.16264 | 0.1658 | 0.1658 | 24.287
527 | 1578 | 0.15572 | 0.16474 | 0.16474 | 23.4476
528 | 1581 | 0.14882 | 0.16368 | 0.16368 | 22.5964
529 | 1584 | 0.14194 | 0.16262 | 0.16262 | 21.7332
530 | 1587 | 0.13508 | 0.16156 | 0.16156 | 20.8578
531 | 1590 | 0.12824 | 0.16051 | 0.16051 | 19.9703
532 | 1593 | 0.12143 | 0.15945 | 0.15945 | 19.0703
533 | 1596 | 0.11464 | 0.1584 | 0.1584 | 18.1579
534 | 1599 | 0.10787 | 0.15734 | 0.15734 | 17.2328
535 | 1602 | 0.10113 | 0.15629 | 0.15629 | 16.295
536 | 1605 | 0.094409 | 0.15524 | 0.15524 | 15.3444
537 | 1608 | 0.087717 | 0.15418 | 0.15418 | 14.3808
538 | 1611 | 0.081052 | 0.15314 | 0.15314 | 13.404
539 | 1614 | 0.074414 | 0.15209 | 0.15209 | 12.4141
540 | 1617 | 0.067805 | 0.15104 | 0.15104 | 11.4109
541 | 1620 | 0.061224 | 0.15 | 0.15 | 10.3943
542 | 1623 | 0.054672 | 0.14896 | 0.14896 | 9.3641
543 | 1626 | 0.048151 | 0.14792 | 0.14792 | 8.3203
544 | 1629 | 0.04166 | 0.14689 | 0.14689 | 7.2629
545 | 1632 | 0.035201 | 0.14586 | 0.14586 | 6.1917
546 | 1635 | 0.028774 | 0.14483 | 0.14483 | 5.1066
547 | 1638 | 0.022381 | 0.1438 | 0.1438 | 4.0075
548 | 1641 | 0.01602 | 0.14278 | 0.14278 | 2.8945
549 | 1644 | 0.0096948 | 0.14176 | 0.14176 | 1.7674
550 | 1647 | 0.0034044 | 0.14074 | 0.14074 | 0.62627
551 | 1650 | -0.0028502 | 0.13973 | 0.13973 | -0.52906
552 | 1653 | -0.0090681 | 0.13873 | 0.13873 | -1.6986
553 | 1656 | -0.015249 | 0.13772 | 0.13772 | -2.8823
554 | 1659 | -0.021391 | 0.13673 | 0.13673 | -4.0802
555 | 1662 | -0.027495 | 0.13573 | 0.13573 | -5.2924
556 | 1665 | -0.033559 | 0.13474 | 0.13474 | -6.5187
557 | 1668 | -0.039583 | 0.13376 | 0.13376 | -7.7593
558 | 1671 | -0.045565 | 0.13278 | 0.13278 | -9.014
559 | 1674 | -0.051506 | 0.13181 | 0.13181 | -10.2828
560 | 1677 | -0.057405 | 0.13085 | 0.13085 | -11.5657
561 | 1680 | -0.06326 | 0.12989 | 0.12989 | -12.8625
562 | 1683 | -0.069071 | 0.12893 | 0.12893 | -14.1732
563 | 1686 | -0.074837 | 0.12799 | 0.12799 | -15.4977
564 | 1689 | -0.080558 | 0.12704 | 0.12704 | -16.8358
565 | 1692 | -0.086232 | 0.12611 | 0.12611 | -18.1873
566 | 1695 | -0.091859 | 0.12518 | 0.12518 | -19.5522
567 | 1698 | -0.097439 | 0.12426 | 0.12426 | -20.9303
568 | 1701 | -0.10297 | 0.12335 | 0.12335 | -22.3212
569 | 1704 | -0.10845 | 0.12245 | 0.12245 | -23.7248
570 | 1707 | -0.11388 | 0.12155 | 0.12155 | -25.1408
571 | 1710 | -0.11926 | 0.12067 | 0.12067 | -26.569
572 | 1713 | -0.12459 | 0.11979 | 0.11979 | -28.009
573 | 1716 | -0.12987 | 0.11891 | 0.11891 | -29.4605
574 | 1719 | -0.13509 | 0.11805 | 0.11805 | -30.9231
575 | 1722 | -0.14026 | 0.1172 | 0.1172 | -32.3965
576 | 1725 | -0.14538 | 0.11636 | 0.11636 | -33.8801
577 | 1728 | -0.15044 | 0.11552 | 0.11552 | -35.3736
578 | 1731 | -0.15544 | 0.1147 | 0.1147 | -36.8765
579 | 1734 | -0.16039 | 0.11389 | 0.11389 | -38.3881
580 | 1737 | -0.16527 | 0.11308 | 0.11308 | -39.9081

## Master
| SP (in w.c.) | Operating BHP (Total) | Operating BHP (Per Fan) |  | Wheel Size (Inches) Max RPM by Class
| 1.2149 | 0.27117 | 0.27117 |  |  | 12 | 13 | 14 | 15 | 16 | 18 | 20 | 22
|  |  |  | I |  | 3525 | 3226 | 3040 | 2854 | 2579 | 2350 | 2143 | 1927
| Peak SP (in w.c.) | Minimum Wheel Housing " |  | II |  | 4596 | 4207 | 3965 | 3722 | 3450 | 3065 | 2794 | 2512
| 1.499 | 16.0008 |  | III |  | 4596 | 4207 | 3965 | 3722 | 3930 | 3862 | 3521 | 3166
See Engineering
| Density | Standard Air BHP
| 0.074996 | 0.27118
|  |  |  | Density | Absolute Pressure
| Static Efficiency (%) | % of Peak Static Pressure |  | 0.074996 | 29.92
| 74.0342 | 81.0452
|  |  |  | 74.0342 | <---static efficiency |  |  |  | Fan selection curves Wheel Max RPM Lookup
| Operating Hz | % of Peak Static Efficiency | [6 empty] | 4596 | Fan Max RPM
| 61.3636 | 100.0745 |  | 100.0745 | <----% of peak static efficiency
Lookup Table
| Wheel Class | Max RPM | Wheel Class
|  |  | I | 12 | 12.25 | 12 |  | 12.25
12 | I | 3525 | Max RPM | 14 | 13.5 | 14
13 | FALSE | FALSE | 3525 | 16 | 16.5 | 16
14 | FALSE | FALSE |  | 18 | 18.25 | 18
15 | FALSE | FALSE |  | 20 | 20 | 20
16 | FALSE | FALSE |  | 22 | 22.25 | 22
18 | FALSE | FALSE
20 | FALSE | FALSE
22 | FALSE | FALSE
Max eff from Interp Curv
73.9791
| SP (in w.c.) | Operating BHP (Total) | Fan Curve Selection Number
100
12 | 1.2149 | 0.27117 | 1
12-50 | 1.2465 | 0.28454 |  | 50 | 0
12-100 | 1.2149 | 0.27117 |  | 100 | 50
50

## Interp Curv
Fan Wheel Size 12-50
| Operating Curve Data Points |  |  |  |  | 100 |  | 0 |  |  |  | 50
|  |  | 1800 |  | RPM
| CFM | SP | BHP | BHP | Efficiency |  | 12-50 Ps |  | 12-50 BHP |  | 12-100 Ps |  | 12-100 BHP
|  |  | TOTAL | PER FAN |  |  |  |  | Per Fan |  |  |  | Per Fan
1 | 0 | 1.4713 | 0.075845 | 0.075845 | 0 |  | 1.5307 |  | 0.10201 | 0 | 1.4713 |  | 0.075845
2 | 6 | 1.475 | 0.078224 | 0.078224 | 1.7785 |  | 1.5315 |  | 0.1042 | 6 | 1.475 |  | 0.078224
3 | 12 | 1.4784 | 0.080548 | 0.080548 | 3.4625 |  | 1.532 |  | 0.10633 | 12 | 1.4784 |  | 0.080548
4 | 18 | 1.4816 | 0.082818 | 0.082818 | 5.062 |  | 1.5323 |  | 0.10841 | 18 | 1.4816 |  | 0.082818
5 | 24 | 1.4844 | 0.085037 | 0.085037 | 6.5856 |  | 1.5324 |  | 0.11042 | 24 | 1.4844 |  | 0.085037
6 | 30 | 1.4869 | 0.087207 | 0.087207 | 8.0409 |  | 1.5323 |  | 0.11239 | 30 | 1.4869 |  | 0.087207
7 | 36 | 1.4891 | 0.089328 | 0.089328 | 9.4342 |  | 1.5319 |  | 0.1143 | 36 | 1.4891 |  | 0.089328
8 | 42 | 1.4911 | 0.091402 | 0.091402 | 10.7712 |  | 1.5313 |  | 0.11616 | 42 | 1.4911 |  | 0.091402
9 | 48 | 1.4929 | 0.093431 | 0.093431 | 12.0566 |  | 1.5306 |  | 0.11798 | 48 | 1.4929 |  | 0.093431
10 | 54 | 1.4944 | 0.095416 | 0.095416 | 13.2948 |  | 1.5297 |  | 0.11975 | 54 | 1.4944 |  | 0.095416
11 | 60 | 1.4956 | 0.097359 | 0.097359 | 14.4894 |  | 1.5286 |  | 0.12148 | 60 | 1.4956 |  | 0.097359
12 | 66 | 1.4967 | 0.099262 | 0.099262 | 15.6439 |  | 1.5274 |  | 0.12316 | 66 | 1.4967 |  | 0.099262
13 | 72 | 1.4975 | 0.10112 | 0.10112 | 16.7611 |  | 1.5261 |  | 0.12481 | 72 | 1.4975 |  | 0.10112
14 | 78 | 1.4982 | 0.10295 | 0.10295 | 17.8436 |  | 1.5246 |  | 0.12641 | 78 | 1.4982 |  | 0.10295
15 | 84 | 1.4986 | 0.10474 | 0.10474 | 18.8939 |  | 1.523 |  | 0.12798 | 84 | 1.4986 |  | 0.10474
16 | 90 | 1.4989 | 0.10649 | 0.10649 | 19.9139 |  | 1.5213 |  | 0.12952 | 90 | 1.4989 |  | 0.10649
17 | 96 | 1.499 | 0.10821 | 0.10821 | 20.9057 |  | 1.5195 |  | 0.13102 | 96 | 1.499 |  | 0.10821
18 | 102 | 1.4989 | 0.10989 | 0.10989 | 21.8708 |  | 1.5176 |  | 0.13249 | 102 | 1.4989 |  | 0.10989
19 | 108 | 1.4987 | 0.11155 | 0.11155 | 22.8109 |  | 1.5156 |  | 0.13393 | 108 | 1.4987 |  | 0.11155
20 | 114 | 1.4984 | 0.11317 | 0.11317 | 23.7272 |  | 1.5136 |  | 0.13534 | 114 | 1.4984 |  | 0.11317
21 | 120 | 1.4979 | 0.11477 | 0.11477 | 24.6211 |  | 1.5115 |  | 0.13672 | 120 | 1.4979 |  | 0.11477
22 | 126 | 1.4973 | 0.11633 | 0.11633 | 25.4938 |  | 1.5093 |  | 0.13808 | 126 | 1.4973 |  | 0.11633
23 | 132 | 1.4966 | 0.11787 | 0.11787 | 26.3463 |  | 1.5071 |  | 0.13941 | 132 | 1.4966 |  | 0.11787
24 | 138 | 1.4958 | 0.11939 | 0.11939 | 27.1795 |  | 1.5048 |  | 0.14072 | 138 | 1.4958 |  | 0.11939
25 | 144 | 1.4948 | 0.12088 | 0.12088 | 27.9944 |  | 1.5025 |  | 0.14201 | 144 | 1.4948 |  | 0.12088
26 | 150 | 1.4938 | 0.12234 | 0.12234 | 28.7917 |  | 1.5002 |  | 0.14328 | 150 | 1.4938 |  | 0.12234
27 | 156 | 1.4927 | 0.12378 | 0.12378 | 29.5723 |  | 1.4978 |  | 0.14453 | 156 | 1.4927 |  | 0.12378
28 | 162 | 1.4915 | 0.12521 | 0.12521 | 30.3367 |  | 1.4955 |  | 0.14576 | 162 | 1.4915 |  | 0.12521
29 | 168 | 1.4903 | 0.12661 | 0.12661 | 31.0858 |  | 1.4931 |  | 0.14697 | 168 | 1.4903 |  | 0.12661
30 | 174 | 1.4889 | 0.12799 | 0.12799 | 31.82 |  | 1.4907 |  | 0.14817 | 174 | 1.4889 |  | 0.12799
31 | 180 | 1.4875 | 0.12935 | 0.12935 | 32.5399 |  | 1.4883 |  | 0.14935 | 180 | 1.4875 |  | 0.12935
32 | 186 | 1.4861 | 0.1307 | 0.1307 | 33.2461 |  | 1.4859 |  | 0.15052 | 186 | 1.4861 |  | 0.1307
33 | 192 | 1.4846 | 0.13202 | 0.13202 | 33.939 |  | 1.4835 |  | 0.15168 | 192 | 1.4846 |  | 0.13202
34 | 198 | 1.483 | 0.13334 | 0.13334 | 34.6191 |  | 1.4812 |  | 0.15282 | 198 | 1.483 |  | 0.13334
35 | 204 | 1.4814 | 0.13463 | 0.13463 | 35.2869 |  | 1.4788 |  | 0.15395 | 204 | 1.4814 |  | 0.13463
36 | 210 | 1.4798 | 0.13591 | 0.13591 | 35.9427 |  | 1.4765 |  | 0.15508 | 210 | 1.4798 |  | 0.13591
37 | 216 | 1.4782 | 0.13718 | 0.13718 | 36.5868 |  | 1.4742 |  | 0.15619 | 216 | 1.4782 |  | 0.13718
38 | 222 | 1.4765 | 0.13844 | 0.13844 | 37.2198 |  | 1.4719 |  | 0.15729 | 222 | 1.4765 |  | 0.13844
39 | 228 | 1.4748 | 0.13968 | 0.13968 | 37.8418 |  | 1.4696 |  | 0.15839 | 228 | 1.4748 |  | 0.13968
40 | 234 | 1.4731 | 0.14092 | 0.14092 | 38.4533 |  | 1.4674 |  | 0.15948 | 234 | 1.4731 |  | 0.14092
41 | 240 | 1.4713 | 0.14214 | 0.14214 | 39.0545 |  | 1.4652 |  | 0.16057 | 240 | 1.4713 |  | 0.14214
42 | 246 | 1.4696 | 0.14335 | 0.14335 | 39.6457 |  | 1.4631 |  | 0.16164 | 246 | 1.4696 |  | 0.14335
43 | 252 | 1.4679 | 0.14455 | 0.14455 | 40.2272 |  | 1.461 |  | 0.16272 | 252 | 1.4679 |  | 0.14455
44 | 258 | 1.4661 | 0.14575 | 0.14575 | 40.7993 |  | 1.4589 |  | 0.16379 | 258 | 1.4661 |  | 0.14575
45 | 264 | 1.4644 | 0.14693 | 0.14693 | 41.3622 |  | 1.4569 |  | 0.16485 | 264 | 1.4644 |  | 0.14693
46 | 270 | 1.4627 | 0.14811 | 0.14811 | 41.9161 |  | 1.455 |  | 0.16592 | 270 | 1.4627 |  | 0.14811
47 | 276 | 1.461 | 0.14928 | 0.14928 | 42.4614 |  | 1.453 |  | 0.16698 | 276 | 1.461 |  | 0.14928
48 | 282 | 1.4592 | 0.15045 | 0.15045 | 42.9981 |  | 1.4512 |  | 0.16804 | 282 | 1.4592 |  | 0.15045
49 | 288 | 1.4575 | 0.15161 | 0.15161 | 43.5266 |  | 1.4494 |  | 0.1691 | 288 | 1.4575 |  | 0.15161
50 | 294 | 1.4559 | 0.15276 | 0.15276 | 44.047 |  | 1.4476 |  | 0.17015 | 294 | 1.4559 |  | 0.15276
51 | 300 | 1.4542 | 0.15391 | 0.15391 | 44.5595 |  | 1.4459 |  | 0.17121 | 300 | 1.4542 |  | 0.15391
52 | 306 | 1.4526 | 0.15505 | 0.15505 | 45.0643 |  | 1.4443 |  | 0.17226 | 306 | 1.4526 |  | 0.15505
53 | 312 | 1.451 | 0.15619 | 0.15619 | 45.5617 |  | 1.4427 |  | 0.17332 | 312 | 1.451 |  | 0.15619
54 | 318 | 1.4494 | 0.15733 | 0.15733 | 46.0517 |  | 1.4412 |  | 0.17438 | 318 | 1.4494 |  | 0.15733
55 | 324 | 1.4478 | 0.15847 | 0.15847 | 46.5345 |  | 1.4397 |  | 0.17544 | 324 | 1.4478 |  | 0.15847
56 | 330 | 1.4463 | 0.1596 | 0.1596 | 47.0104 |  | 1.4383 |  | 0.1765 | 330 | 1.4463 |  | 0.1596
57 | 336 | 1.4448 | 0.16073 | 0.16073 | 47.4795 |  | 1.437 |  | 0.17756 | 336 | 1.4448 |  | 0.16073
58 | 342 | 1.4433 | 0.16186 | 0.16186 | 47.9418 |  | 1.4357 |  | 0.17862 | 342 | 1.4433 |  | 0.16186
59 | 348 | 1.4419 | 0.16298 | 0.16298 | 48.3977 |  | 1.4345 |  | 0.17969 | 348 | 1.4419 |  | 0.16298
60 | 354 | 1.4405 | 0.16411 | 0.16411 | 48.8472 |  | 1.4333 |  | 0.18076 | 354 | 1.4405 |  | 0.16411
61 | 360 | 1.4391 | 0.16523 | 0.16523 | 49.2904 |  | 1.4322 |  | 0.18183 | 360 | 1.4391 |  | 0.16523
62 | 366 | 1.4378 | 0.16636 | 0.16636 | 49.7276 |  | 1.4311 |  | 0.1829 | 366 | 1.4378 |  | 0.16636
63 | 372 | 1.4365 | 0.16748 | 0.16748 | 50.1588 |  | 1.4301 |  | 0.18398 | 372 | 1.4365 |  | 0.16748
64 | 378 | 1.4353 | 0.1686 | 0.1686 | 50.5842 |  | 1.4292 |  | 0.18506 | 378 | 1.4353 |  | 0.1686
65 | 384 | 1.4341 | 0.16973 | 0.16973 | 51.0039 |  | 1.4283 |  | 0.18614 | 384 | 1.4341 |  | 0.16973
66 | 390 | 1.4329 | 0.17085 | 0.17085 | 51.418 |  | 1.4275 |  | 0.18723 | 390 | 1.4329 |  | 0.17085
67 | 396 | 1.4318 | 0.17197 | 0.17197 | 51.8266 |  | 1.4267 |  | 0.18832 | 396 | 1.4318 |  | 0.17197
68 | 402 | 1.4307 | 0.1731 | 0.1731 | 52.2299 |  | 1.426 |  | 0.18942 | 402 | 1.4307 |  | 0.1731
69 | 408 | 1.4296 | 0.17423 | 0.17423 | 52.628 |  | 1.4254 |  | 0.19051 | 408 | 1.4296 |  | 0.17423
70 | 414 | 1.4286 | 0.17535 | 0.17535 | 53.021 |  | 1.4248 |  | 0.19162 | 414 | 1.4286 |  | 0.17535
71 | 420 | 1.4276 | 0.17648 | 0.17648 | 53.4089 |  | 1.4242 |  | 0.19272 | 420 | 1.4276 |  | 0.17648
72 | 426 | 1.4267 | 0.17761 | 0.17761 | 53.7919 |  | 1.4237 |  | 0.19383 | 426 | 1.4267 |  | 0.17761
73 | 432 | 1.4258 | 0.17874 | 0.17874 | 54.1701 |  | 1.4232 |  | 0.19494 | 432 | 1.4258 |  | 0.17874
74 | 438 | 1.4249 | 0.17988 | 0.17988 | 54.5436 |  | 1.4228 |  | 0.19606 | 438 | 1.4249 |  | 0.17988
75 | 444 | 1.4241 | 0.18101 | 0.18101 | 54.9124 |  | 1.4224 |  | 0.19718 | 444 | 1.4241 |  | 0.18101
76 | 450 | 1.4233 | 0.18215 | 0.18215 | 55.2768 |  | 1.4221 |  | 0.19831 | 450 | 1.4233 |  | 0.18215
77 | 456 | 1.4226 | 0.18328 | 0.18328 | 55.6367 |  | 1.4218 |  | 0.19944 | 456 | 1.4226 |  | 0.18328
78 | 462 | 1.4218 | 0.18442 | 0.18442 | 55.9922 |  | 1.4216 |  | 0.20057 | 462 | 1.4218 |  | 0.18442
79 | 468 | 1.4212 | 0.18557 | 0.18557 | 56.3434 |  | 1.4214 |  | 0.2017 | 468 | 1.4212 |  | 0.18557
80 | 474 | 1.4205 | 0.18671 | 0.18671 | 56.6904 |  | 1.4212 |  | 0.20284 | 474 | 1.4205 |  | 0.18671
81 | 480 | 1.4199 | 0.18785 | 0.18785 | 57.0334 |  | 1.4211 |  | 0.20398 | 480 | 1.4199 |  | 0.18785
82 | 486 | 1.4193 | 0.189 | 0.189 | 57.3722 |  | 1.4209 |  | 0.20513 | 486 | 1.4193 |  | 0.189
83 | 492 | 1.4188 | 0.19015 | 0.19015 | 57.7071 |  | 1.4209 |  | 0.20627 | 492 | 1.4188 |  | 0.19015
84 | 498 | 1.4182 | 0.1913 | 0.1913 | 58.0381 |  | 1.4208 |  | 0.20742 | 498 | 1.4182 |  | 0.1913
85 | 504 | 1.4177 | 0.19245 | 0.19245 | 58.3652 |  | 1.4208 |  | 0.20858 | 504 | 1.4177 |  | 0.19245
86 | 510 | 1.4173 | 0.19361 | 0.19361 | 58.6885 |  | 1.4208 |  | 0.20973 | 510 | 1.4173 |  | 0.19361
87 | 516 | 1.4168 | 0.19476 | 0.19476 | 59.0081 |  | 1.4208 |  | 0.21089 | 516 | 1.4168 |  | 0.19476
88 | 522 | 1.4164 | 0.19592 | 0.19592 | 59.3241 |  | 1.4208 |  | 0.21205 | 522 | 1.4164 |  | 0.19592
89 | 528 | 1.416 | 0.19708 | 0.19708 | 59.6364 |  | 1.4209 |  | 0.21321 | 528 | 1.416 |  | 0.19708
90 | 534 | 1.4156 | 0.19824 | 0.19824 | 59.9452 |  | 1.421 |  | 0.21437 | 534 | 1.4156 |  | 0.19824
91 | 540 | 1.4152 | 0.1994 | 0.1994 | 60.2504 |  | 1.421 |  | 0.21553 | 540 | 1.4152 |  | 0.1994
92 | 546 | 1.4149 | 0.20056 | 0.20056 | 60.5523 |  | 1.4211 |  | 0.2167 | 546 | 1.4149 |  | 0.20056
93 | 552 | 1.4146 | 0.20172 | 0.20172 | 60.8506 |  | 1.4212 |  | 0.21787 | 552 | 1.4146 |  | 0.20172
94 | 558 | 1.4142 | 0.20288 | 0.20288 | 61.1457 |  | 1.4213 |  | 0.21903 | 558 | 1.4142 |  | 0.20288
95 | 564 | 1.4139 | 0.20405 | 0.20405 | 61.4373 |  | 1.4214 |  | 0.2202 | 564 | 1.4139 |  | 0.20405
96 | 570 | 1.4136 | 0.20521 | 0.20521 | 61.7257 |  | 1.4216 |  | 0.22136 | 570 | 1.4136 |  | 0.20521
97 | 576 | 1.4133 | 0.20637 | 0.20637 | 62.0108 |  | 1.4217 |  | 0.22253 | 576 | 1.4133 |  | 0.20637
98 | 582 | 1.413 | 0.20754 | 0.20754 | 62.2927 |  | 1.4218 |  | 0.2237 | 582 | 1.413 |  | 0.20754
99 | 588 | 1.4128 | 0.2087 | 0.2087 | 62.5715 |  | 1.4218 |  | 0.22486 | 588 | 1.4128 |  | 0.2087
100 | 594 | 1.4125 | 0.20986 | 0.20986 | 62.847 |  | 1.4219 |  | 0.22602 | 594 | 1.4125 |  | 0.20986
101 | 600 | 1.4122 | 0.21102 | 0.21102 | 63.1194 |  | 1.422 |  | 0.22719 | 600 | 1.4122 |  | 0.21102
102 | 606 | 1.4119 | 0.21218 | 0.21218 | 63.3887 |  | 1.4221 |  | 0.22835 | 606 | 1.4119 |  | 0.21218
103 | 612 | 1.4116 | 0.21334 | 0.21334 | 63.6548 |  | 1.4221 |  | 0.2295 | 612 | 1.4116 |  | 0.21334
104 | 618 | 1.4113 | 0.2145 | 0.2145 | 63.918 |  | 1.4221 |  | 0.23066 | 618 | 1.4113 |  | 0.2145
105 | 624 | 1.411 | 0.21566 | 0.21566 | 64.178 |  | 1.4221 |  | 0.23181 | 624 | 1.411 |  | 0.21566
106 | 630 | 1.4106 | 0.21681 | 0.21681 | 64.435 |  | 1.4221 |  | 0.23296 | 630 | 1.4106 |  | 0.21681
107 | 636 | 1.4103 | 0.21796 | 0.21796 | 64.689 |  | 1.422 |  | 0.23411 | 636 | 1.4103 |  | 0.21796
108 | 642 | 1.4099 | 0.21911 | 0.21911 | 64.94 |  | 1.422 |  | 0.23525 | 642 | 1.4099 |  | 0.21911
109 | 648 | 1.4095 | 0.22026 | 0.22026 | 65.1879 |  | 1.4218 |  | 0.23639 | 648 | 1.4095 |  | 0.22026
110 | 654 | 1.4091 | 0.2214 | 0.2214 | 65.4329 |  | 1.4217 |  | 0.23752 | 654 | 1.4091 |  | 0.2214
111 | 660 | 1.4087 | 0.22254 | 0.22254 | 65.6749 |  | 1.4215 |  | 0.23865 | 660 | 1.4087 |  | 0.22254
112 | 666 | 1.4082 | 0.22368 | 0.22368 | 65.9139 |  | 1.4213 |  | 0.23977 | 666 | 1.4082 |  | 0.22368
113 | 672 | 1.4077 | 0.22481 | 0.22481 | 66.1499 |  | 1.421 |  | 0.24089 | 672 | 1.4077 |  | 0.22481
114 | 678 | 1.4072 | 0.22594 | 0.22594 | 66.3829 |  | 1.4207 |  | 0.242 | 678 | 1.4072 |  | 0.22594
115 | 684 | 1.4067 | 0.22706 | 0.22706 | 66.6129 |  | 1.4204 |  | 0.24311 | 684 | 1.4067 |  | 0.22706
116 | 690 | 1.4061 | 0.22818 | 0.22818 | 66.8399 |  | 1.42 |  | 0.24421 | 690 | 1.4061 |  | 0.22818
117 | 696 | 1.4054 | 0.22929 | 0.22929 | 67.064 |  | 1.4195 |  | 0.2453 | 696 | 1.4054 |  | 0.22929
118 | 702 | 1.4048 | 0.2304 | 0.2304 | 67.285 |  | 1.419 |  | 0.24638 | 702 | 1.4048 |  | 0.2304
119 | 708 | 1.404 | 0.2315 | 0.2315 | 67.503 |  | 1.4185 |  | 0.24746 | 708 | 1.404 |  | 0.2315
120 | 714 | 1.4033 | 0.23259 | 0.23259 | 67.718 |  | 1.4179 |  | 0.24852 | 714 | 1.4033 |  | 0.23259
121 | 720 | 1.4025 | 0.23368 | 0.23368 | 67.93 |  | 1.4172 |  | 0.24958 | 720 | 1.4025 |  | 0.23368
122 | 726 | 1.4016 | 0.23476 | 0.23476 | 68.1389 |  | 1.4165 |  | 0.25063 | 726 | 1.4016 |  | 0.23476
123 | 732 | 1.4007 | 0.23583 | 0.23583 | 68.3448 |  | 1.4157 |  | 0.25167 | 732 | 1.4007 |  | 0.23583
124 | 738 | 1.3997 | 0.23689 | 0.23689 | 68.5476 |  | 1.4148 |  | 0.25271 | 738 | 1.3997 |  | 0.23689
125 | 744 | 1.3986 | 0.23795 | 0.23795 | 68.7473 |  | 1.4139 |  | 0.25373 | 744 | 1.3986 |  | 0.23795
126 | 750 | 1.3975 | 0.23899 | 0.23899 | 68.9439 |  | 1.4129 |  | 0.25474 | 750 | 1.3975 |  | 0.23899
127 | 756 | 1.3964 | 0.24003 | 0.24003 | 69.1373 |  | 1.4118 |  | 0.25574 | 756 | 1.3964 |  | 0.24003
128 | 762 | 1.3951 | 0.24106 | 0.24106 | 69.3276 |  | 1.4107 |  | 0.25673 | 762 | 1.3951 |  | 0.24106
129 | 768 | 1.3938 | 0.24207 | 0.24207 | 69.5147 |  | 1.4095 |  | 0.2577 | 768 | 1.3938 |  | 0.24207
130 | 774 | 1.3925 | 0.24308 | 0.24308 | 69.6986 |  | 1.4082 |  | 0.25867 | 774 | 1.3925 |  | 0.24308
131 | 780 | 1.391 | 0.24408 | 0.24408 | 69.8792 |  | 1.4068 |  | 0.25962 | 780 | 1.391 |  | 0.24408
132 | 786 | 1.3895 | 0.24506 | 0.24506 | 70.0566 |  | 1.4054 |  | 0.26056 | 786 | 1.3895 |  | 0.24506
133 | 792 | 1.3879 | 0.24604 | 0.24604 | 70.2307 |  | 1.4039 |  | 0.26149 | 792 | 1.3879 |  | 0.24604
134 | 798 | 1.3862 | 0.247 | 0.247 | 70.4015 |  | 1.4023 |  | 0.2624 | 798 | 1.3862 |  | 0.247
135 | 804 | 1.3844 | 0.24795 | 0.24795 | 70.5689 |  | 1.4006 |  | 0.2633 | 804 | 1.3844 |  | 0.24795
136 | 810 | 1.3826 | 0.24889 | 0.24889 | 70.7329 |  | 1.3988 |  | 0.26419 | 810 | 1.3826 |  | 0.24889
137 | 816 | 1.3806 | 0.24981 | 0.24981 | 70.8935 |  | 1.3969 |  | 0.26506 | 816 | 1.3806 |  | 0.24981
138 | 822 | 1.3786 | 0.25072 | 0.25072 | 71.0507 |  | 1.395 |  | 0.26592 | 822 | 1.3786 |  | 0.25072
139 | 828 | 1.3764 | 0.25161 | 0.25161 | 71.2043 |  | 1.393 |  | 0.26676 | 828 | 1.3764 |  | 0.25161
140 | 834 | 1.3742 | 0.2525 | 0.2525 | 71.3544 |  | 1.3908 |  | 0.26758 | 834 | 1.3742 |  | 0.2525
141 | 840 | 1.3719 | 0.25336 | 0.25336 | 71.5009 |  | 1.3886 |  | 0.26839 | 840 | 1.3719 |  | 0.25336
142 | 846 | 1.3695 | 0.25421 | 0.25421 | 71.6438 |  | 1.3863 |  | 0.26919 | 846 | 1.3695 |  | 0.25421
143 | 852 | 1.3669 | 0.25505 | 0.25505 | 71.783 |  | 1.3839 |  | 0.26996 | 852 | 1.3669 |  | 0.25505
144 | 858 | 1.3643 | 0.25587 | 0.25587 | 71.9185 |  | 1.3814 |  | 0.27072 | 858 | 1.3643 |  | 0.25587
145 | 864 | 1.3616 | 0.25667 | 0.25667 | 72.0502 |  | 1.3788 |  | 0.27147 | 864 | 1.3616 |  | 0.25667
146 | 870 | 1.3587 | 0.25745 | 0.25745 | 72.1782 |  | 1.3761 |  | 0.27219 | 870 | 1.3587 |  | 0.25745
147 | 876 | 1.3558 | 0.25822 | 0.25822 | 72.3023 |  | 1.3733 |  | 0.2729 | 876 | 1.3558 |  | 0.25822
148 | 882 | 1.3527 | 0.25897 | 0.25897 | 72.4224 |  | 1.3704 |  | 0.27359 | 882 | 1.3527 |  | 0.25897
149 | 888 | 1.3495 | 0.25971 | 0.25971 | 72.5386 |  | 1.3674 |  | 0.27426 | 888 | 1.3495 |  | 0.25971
150 | 894 | 1.3462 | 0.26042 | 0.26042 | 72.6509 |  | 1.3642 |  | 0.27492 | 894 | 1.3462 |  | 0.26042
151 | 900 | 1.3428 | 0.26111 | 0.26111 | 72.759 |  | 1.361 |  | 0.27555 | 900 | 1.3428 |  | 0.26111
152 | 906 | 1.3393 | 0.26179 | 0.26179 | 72.863 |  | 1.3577 |  | 0.27617 | 906 | 1.3393 |  | 0.26179
153 | 912 | 1.3356 | 0.26244 | 0.26244 | 72.9628 |  | 1.3543 |  | 0.27676 | 912 | 1.3356 |  | 0.26244
154 | 918 | 1.3319 | 0.26308 | 0.26308 | 73.0584 |  | 1.3508 |  | 0.27734 | 918 | 1.3319 |  | 0.26308
155 | 924 | 1.328 | 0.26369 | 0.26369 | 73.1497 |  | 1.3472 |  | 0.27789 | 924 | 1.328 |  | 0.26369
156 | 930 | 1.3239 | 0.26429 | 0.26429 | 73.2367 |  | 1.3435 |  | 0.27843 | 930 | 1.3239 |  | 0.26429
157 | 936 | 1.3198 | 0.26486 | 0.26486 | 73.3192 |  | 1.3396 |  | 0.27894 | 936 | 1.3198 |  | 0.26486
158 | 942 | 1.3155 | 0.26541 | 0.26541 | 73.3972 |  | 1.3357 |  | 0.27944 | 942 | 1.3155 |  | 0.26541
159 | 948 | 1.3111 | 0.26594 | 0.26594 | 73.4707 |  | 1.3316 |  | 0.27991 | 948 | 1.3111 |  | 0.26594
160 | 954 | 1.3066 | 0.26644 | 0.26644 | 73.5395 |  | 1.3275 |  | 0.28036 | 954 | 1.3066 |  | 0.26644
161 | 960 | 1.3019 | 0.26693 | 0.26693 | 73.6037 |  | 1.3232 |  | 0.28079 | 960 | 1.3019 |  | 0.26693
162 | 966 | 1.2971 | 0.26739 | 0.26739 | 73.663 |  | 1.3189 |  | 0.2812 | 966 | 1.2971 |  | 0.26739
163 | 972 | 1.2921 | 0.26782 | 0.26782 | 73.7176 |  | 1.3144 |  | 0.28159 | 972 | 1.2921 |  | 0.26782
164 | 978 | 1.287 | 0.26823 | 0.26823 | 73.7672 |  | 1.3098 |  | 0.28195 | 978 | 1.287 |  | 0.26823
165 | 984 | 1.2818 | 0.26862 | 0.26862 | 73.8118 |  | 1.3051 |  | 0.2823 | 984 | 1.2818 |  | 0.26862
166 | 990 | 1.2764 | 0.26898 | 0.26898 | 73.8513 |  | 1.3003 |  | 0.28261 | 990 | 1.2764 |  | 0.26898
167 | 996 | 1.2709 | 0.26932 | 0.26932 | 73.8857 |  | 1.2954 |  | 0.28291 | 996 | 1.2709 |  | 0.26932
168 | 1002 | 1.2653 | 0.26963 | 0.26963 | 73.9149 |  | 1.2904 |  | 0.28319 | 1002 | 1.2653 |  | 0.26963
169 | 1008 | 1.2595 | 0.26992 | 0.26992 | 73.9387 |  | 1.2853 |  | 0.28344 | 1008 | 1.2595 |  | 0.26992
170 | 1014 | 1.2535 | 0.27018 | 0.27018 | 73.9571 |  | 1.2801 |  | 0.28367 | 1014 | 1.2535 |  | 0.27018
171 | 1020 | 1.2475 | 0.27041 | 0.27041 | 73.9701 |  | 1.2748 |  | 0.28387 | 1020 | 1.2475 |  | 0.27041
172 | 1026 | 1.2412 | 0.27062 | 0.27062 | 73.9774 |  | 1.2693 |  | 0.28405 | 1026 | 1.2412 |  | 0.27062
173 | 1032 | 1.2349 | 0.2708 | 0.2708 | 73.9791 |  | 1.2638 |  | 0.28421 | 1032 | 1.2349 |  | 0.2708
174 | 1038 | 1.2283 | 0.27095 | 0.27095 | 73.9749 |  | 1.2581 |  | 0.28434 | 1038 | 1.2283 |  | 0.27095
175 | 1044 | 1.2217 | 0.27107 | 0.27107 | 73.9649 |  | 1.2524 |  | 0.28445 | 1044 | 1.2217 |  | 0.27107
176 | 1050 | 1.2149 | 0.27117 | 0.27117 | 73.9489 |  | 1.2465 |  | 0.28454 | 1050 | 1.2149 |  | 0.27117
177 | 1056 | 1.2079 | 0.27124 | 0.27124 | 73.9269 |  | 1.2406 |  | 0.2846 | 1056 | 1.2079 |  | 0.27124
178 | 1062 | 1.2008 | 0.27127 | 0.27127 | 73.8986 |  | 1.2345 |  | 0.28464 | 1062 | 1.2008 |  | 0.27127
179 | 1068 | 1.1935 | 0.27129 | 0.27129 | 73.864 |  | 1.2283 |  | 0.28466 | 1068 | 1.1935 |  | 0.27129
180 | 1074 | 1.1861 | 0.27127 | 0.27127 | 73.8231 |  | 1.2221 |  | 0.28465 | 1074 | 1.1861 |  | 0.27127
181 | 1080 | 1.1786 | 0.27122 | 0.27122 | 73.7756 |  | 1.2157 |  | 0.28461 | 1080 | 1.1786 |  | 0.27122
182 | 1086 | 1.1709 | 0.27114 | 0.27114 | 73.7214 |  | 1.2092 |  | 0.28455 | 1086 | 1.1709 |  | 0.27114
183 | 1092 | 1.163 | 0.27103 | 0.27103 | 73.6606 |  | 1.2026 |  | 0.28447 | 1092 | 1.163 |  | 0.27103
184 | 1098 | 1.155 | 0.27089 | 0.27089 | 73.5928 |  | 1.196 |  | 0.28436 | 1098 | 1.155 |  | 0.27089
185 | 1104 | 1.1468 | 0.27073 | 0.27073 | 73.518 |  | 1.1892 |  | 0.28423 | 1104 | 1.1468 |  | 0.27073
186 | 1110 | 1.1385 | 0.27053 | 0.27053 | 73.4361 |  | 1.1823 |  | 0.28407 | 1110 | 1.1385 |  | 0.27053
187 | 1116 | 1.1301 | 0.2703 | 0.2703 | 73.3468 |  | 1.1754 |  | 0.28389 | 1116 | 1.1301 |  | 0.2703
188 | 1122 | 1.1215 | 0.27004 | 0.27004 | 73.2502 |  | 1.1683 |  | 0.28368 | 1122 | 1.1215 |  | 0.27004
189 | 1128 | 1.1127 | 0.26975 | 0.26975 | 73.146 |  | 1.1611 |  | 0.28345 | 1128 | 1.1127 |  | 0.26975
190 | 1134 | 1.1038 | 0.26942 | 0.26942 | 73.0342 |  | 1.1539 |  | 0.2832 | 1134 | 1.1038 |  | 0.26942
191 | 1140 | 1.0948 | 0.26907 | 0.26907 | 72.9144 |  | 1.1465 |  | 0.28292 | 1140 | 1.0948 |  | 0.26907
192 | 1146 | 1.0856 | 0.26868 | 0.26868 | 72.7867 |  | 1.1391 |  | 0.28262 | 1146 | 1.0856 |  | 0.26868
193 | 1152 | 1.0762 | 0.26827 | 0.26827 | 72.6508 |  | 1.1316 |  | 0.28229 | 1152 | 1.0762 |  | 0.26827
194 | 1158 | 1.0667 | 0.26782 | 0.26782 | 72.5066 |  | 1.124 |  | 0.28194 | 1158 | 1.0667 |  | 0.26782
195 | 1164 | 1.0571 | 0.26733 | 0.26733 | 72.3539 |  | 1.1162 |  | 0.28156 | 1164 | 1.0571 |  | 0.26733
196 | 1170 | 1.0473 | 0.26682 | 0.26682 | 72.1926 |  | 1.1084 |  | 0.28116 | 1170 | 1.0473 |  | 0.26682
197 | 1176 | 1.0374 | 0.26627 | 0.26627 | 72.0224 |  | 1.1006 |  | 0.28074 | 1176 | 1.0374 |  | 0.26627
198 | 1182 | 1.0273 | 0.2657 | 0.2657 | 71.8432 |  | 1.0926 |  | 0.28029 | 1182 | 1.0273 |  | 0.2657
199 | 1188 | 1.0171 | 0.26509 | 0.26509 | 71.6548 |  | 1.0845 |  | 0.27981 | 1188 | 1.0171 |  | 0.26509
200 | 1194 | 1.0067 | 0.26444 | 0.26444 | 71.457 |  | 1.0764 |  | 0.27932 | 1194 | 1.0067 |  | 0.26444
201 | 1200 | 0.99625 | 0.26377 | 0.26377 | 71.2496 |  | 1.0681 |  | 0.2788 | 1200 | 0.99625 |  | 0.26377
202 | 1206 | 0.98562 | 0.26306 | 0.26306 | 71.0325 |  | 1.0598 |  | 0.27825 | 1206 | 0.98562 |  | 0.26306
203 | 1212 | 0.97485 | 0.26232 | 0.26232 | 70.8053 |  | 1.0514 |  | 0.27769 | 1212 | 0.97485 |  | 0.26232
204 | 1218 | 0.96395 | 0.26155 | 0.26155 | 70.5679 |  | 1.043 |  | 0.2771 | 1218 | 0.96395 |  | 0.26155
205 | 1224 | 0.95291 | 0.26074 | 0.26074 | 70.3201 |  | 1.0344 |  | 0.27648 | 1224 | 0.95291 |  | 0.26074
206 | 1230 | 0.94174 | 0.2599 | 0.2599 | 70.0616 |  | 1.0258 |  | 0.27585 | 1230 | 0.94174 |  | 0.2599
207 | 1236 | 0.93044 | 0.25903 | 0.25903 | 69.7922 |  | 1.0171 |  | 0.27519 | 1236 | 0.93044 |  | 0.25903
208 | 1242 | 0.919 | 0.25813 | 0.25813 | 69.5116 |  | 1.0083 |  | 0.27451 | 1242 | 0.919 |  | 0.25813
209 | 1248 | 0.90744 | 0.25719 | 0.25719 | 69.2197 |  | 0.99944 |  | 0.2738 | 1248 | 0.90744 |  | 0.25719
210 | 1254 | 0.89576 | 0.25622 | 0.25622 | 68.9161 |  | 0.99051 |  | 0.27308 | 1254 | 0.89576 |  | 0.25622
211 | 1260 | 0.88395 | 0.25522 | 0.25522 | 68.6006 |  | 0.98151 |  | 0.27233 | 1260 | 0.88395 |  | 0.25522
212 | 1266 | 0.87202 | 0.25419 | 0.25419 | 68.2729 |  | 0.97243 |  | 0.27156 | 1266 | 0.87202 |  | 0.25419
213 | 1272 | 0.85996 | 0.25313 | 0.25313 | 67.9327 |  | 0.96328 |  | 0.27077 | 1272 | 0.85996 |  | 0.25313
214 | 1278 | 0.84779 | 0.25203 | 0.25203 | 67.5798 |  | 0.95406 |  | 0.26996 | 1278 | 0.84779 |  | 0.25203
215 | 1284 | 0.83551 | 0.2509 | 0.2509 | 67.2138 |  | 0.94477 |  | 0.26913 | 1284 | 0.83551 |  | 0.2509
216 | 1290 | 0.8231 | 0.24975 | 0.24975 | 66.8344 |  | 0.93542 |  | 0.26827 | 1290 | 0.8231 |  | 0.24975
217 | 1296 | 0.81059 | 0.24855 | 0.24855 | 66.4413 |  | 0.92599 |  | 0.2674 | 1296 | 0.81059 |  | 0.24855
218 | 1302 | 0.79797 | 0.24733 | 0.24733 | 66.0342 |  | 0.9165 |  | 0.2665 | 1302 | 0.79797 |  | 0.24733
219 | 1308 | 0.78524 | 0.24608 | 0.24608 | 65.6127 |  | 0.90694 |  | 0.26559 | 1308 | 0.78524 |  | 0.24608
220 | 1314 | 0.77241 | 0.2448 | 0.2448 | 65.1766 |  | 0.89732 |  | 0.26466 | 1314 | 0.77241 |  | 0.2448
221 | 1320 | 0.75948 | 0.24348 | 0.24348 | 64.7253 |  | 0.88763 |  | 0.2637 | 1320 | 0.75948 |  | 0.24348
222 | 1326 | 0.74645 | 0.24214 | 0.24214 | 64.2586 |  | 0.87788 |  | 0.26273 | 1326 | 0.74645 |  | 0.24214
223 | 1332 | 0.73332 | 0.24076 | 0.24076 | 63.776 |  | 0.86807 |  | 0.26174 | 1332 | 0.73332 |  | 0.24076
224 | 1338 | 0.7201 | 0.23936 | 0.23936 | 63.2772 |  | 0.85819 |  | 0.26073 | 1338 | 0.7201 |  | 0.23936
225 | 1344 | 0.70679 | 0.23793 | 0.23793 | 62.7618 |  | 0.84825 |  | 0.25971 | 1344 | 0.70679 |  | 0.23793
226 | 1350 | 0.69339 | 0.23647 | 0.23647 | 62.2293 |  | 0.83824 |  | 0.25866 | 1350 | 0.69339 |  | 0.23647
227 | 1356 | 0.67991 | 0.23498 | 0.23498 | 61.6793 |  | 0.82818 |  | 0.2576 | 1356 | 0.67991 |  | 0.23498
228 | 1362 | 0.66634 | 0.23346 | 0.23346 | 61.1113 |  | 0.81805 |  | 0.25652 | 1362 | 0.66634 |  | 0.23346
229 | 1368 | 0.6527 | 0.23191 | 0.23191 | 60.5249 |  | 0.80786 |  | 0.25543 | 1368 | 0.6527 |  | 0.23191
230 | 1374 | 0.63899 | 0.23034 | 0.23034 | 59.9196 |  | 0.79761 |  | 0.25432 | 1374 | 0.63899 |  | 0.23034
231 | 1380 | 0.6252 | 0.22873 | 0.22873 | 59.2948 |  | 0.7873 |  | 0.25319 | 1380 | 0.6252 |  | 0.22873
232 | 1386 | 0.61134 | 0.22711 | 0.22711 | 58.6502 |  | 0.77693 |  | 0.25205 | 1386 | 0.61134 |  | 0.22711
233 | 1392 | 0.59742 | 0.22545 | 0.22545 | 57.9851 |  | 0.7665 |  | 0.25089 | 1392 | 0.59742 |  | 0.22545
234 | 1398 | 0.58344 | 0.22377 | 0.22377 | 57.299 |  | 0.756 |  | 0.24972 | 1398 | 0.58344 |  | 0.22377
235 | 1404 | 0.5694 | 0.22207 | 0.22207 | 56.5913 |  | 0.74544 |  | 0.24853 | 1404 | 0.5694 |  | 0.22207
236 | 1410 | 0.55531 | 0.22034 | 0.22034 | 55.8615 |  | 0.73483 |  | 0.24733 | 1410 | 0.55531 |  | 0.22034
237 | 1416 | 0.54116 | 0.21859 | 0.21859 | 55.109 |  | 0.72414 |  | 0.24612 | 1416 | 0.54116 |  | 0.21859
238 | 1422 | 0.52698 | 0.21681 | 0.21681 | 54.3331 |  | 0.7134 |  | 0.2449 | 1422 | 0.52698 |  | 0.21681
239 | 1428 | 0.51274 | 0.21501 | 0.21501 | 53.5332 |  | 0.70259 |  | 0.24366 | 1428 | 0.51274 |  | 0.21501
240 | 1434 | 0.49847 | 0.21319 | 0.21319 | 52.7086 |  | 0.69172 |  | 0.24241 | 1434 | 0.49847 |  | 0.21319
241 | 1440 | 0.48417 | 0.21134 | 0.21134 | 51.8587 |  | 0.68078 |  | 0.24115 | 1440 | 0.48417 |  | 0.21134
242 | 1446 | 0.46983 | 0.20948 | 0.20948 | 50.9827 |  | 0.66978 |  | 0.23988 | 1446 | 0.46983 |  | 0.20948
243 | 1452 | 0.45547 | 0.20759 | 0.20759 | 50.0801 |  | 0.65871 |  | 0.23859 | 1452 | 0.45547 |  | 0.20759
244 | 1458 | 0.44109 | 0.20569 | 0.20569 | 49.1499 |  | 0.64757 |  | 0.2373 | 1458 | 0.44109 |  | 0.20569
245 | 1464 | 0.42669 | 0.20377 | 0.20377 | 48.1914 |  | 0.63636 |  | 0.236 | 1464 | 0.42669 |  | 0.20377
246 | 1470 | 0.41227 | 0.20182 | 0.20182 | 47.204 |  | 0.62507 |  | 0.23469 | 1470 | 0.41227 |  | 0.20182
247 | 1476 | 0.39785 | 0.19987 | 0.19987 | 46.1866 |  | 0.61372 |  | 0.23337 | 1476 | 0.39785 |  | 0.19987
248 | 1482 | 0.38342 | 0.19789 | 0.19789 | 45.1387 |  | 0.60229 |  | 0.23204 | 1482 | 0.38342 |  | 0.19789
249 | 1488 | 0.36899 | 0.1959 | 0.1959 | 44.0592 |  | 0.59078 |  | 0.2307 | 1488 | 0.36899 |  | 0.1959
250 | 1494 | 0.35456 | 0.19389 | 0.19389 | 42.9473 |  | 0.5792 |  | 0.22936 | 1494 | 0.35456 |  | 0.19389
251 | 1500 | 0.34014 | 0.19187 | 0.19187 | 41.8022 |  | 0.56754 |  | 0.22801 | 1500 | 0.34014 |  | 0.19187
252 | 1506 | 0.32574 | 0.18984 | 0.18984 | 40.6228 |  | 0.55579 |  | 0.22666 | 1506 | 0.32574 |  | 0.18984
253 | 1512 | 0.31135 | 0.18779 | 0.18779 | 39.4084 |  | 0.54395 |  | 0.2253 | 1512 | 0.31135 |  | 0.18779
254 | 1518 | 0.29699 | 0.18573 | 0.18573 | 38.1579 |  | 0.53203 |  | 0.22393 | 1518 | 0.29699 |  | 0.18573
255 | 1524 | 0.28266 | 0.18366 | 0.18366 | 36.8703 |  | 0.52002 |  | 0.22256 | 1524 | 0.28266 |  | 0.18366
256 | 1530 | 0.26835 | 0.18158 | 0.18158 | 35.5447 |  | 0.50791 |  | 0.22119 | 1530 | 0.26835 |  | 0.18158
257 | 1536 | 0.25409 | 0.1795 | 0.1795 | 34.1801 |  | 0.49571 |  | 0.21981 | 1536 | 0.25409 |  | 0.1795
258 | 1542 | 0.23987 | 0.1774 | 0.1774 | 32.7754 |  | 0.48341 |  | 0.21843 | 1542 | 0.23987 |  | 0.1774
259 | 1548 | 0.22569 | 0.1753 | 0.1753 | 31.3296 |  | 0.471 |  | 0.21705 | 1548 | 0.22569 |  | 0.1753
260 | 1554 | 0.21157 | 0.1732 | 0.1732 | 29.8417 |  | 0.45849 |  | 0.21567 | 1554 | 0.21157 |  | 0.1732
261 | 1560 | 0.19751 | 0.17109 | 0.17109 | 28.3106 |  | 0.44586 |  | 0.21429 | 1560 | 0.19751 |  | 0.17109
262 | 1566 | 0.18351 | 0.16897 | 0.16897 | 26.7353 |  | 0.43312 |  | 0.2129 | 1566 | 0.18351 |  | 0.16897
263 | 1572 | 0.16957 | 0.16686 | 0.16686 | 25.1146 |  | 0.42026 |  | 0.21152 | 1572 | 0.16957 |  | 0.16686
264 | 1578 | 0.15572 | 0.16474 | 0.16474 | 23.4476 |  | 0.40728 |  | 0.21013 | 1578 | 0.15572 |  | 0.16474
265 | 1584 | 0.14194 | 0.16262 | 0.16262 | 21.7332 |  | 0.39416 |  | 0.20875 | 1584 | 0.14194 |  | 0.16262
266 | 1590 | 0.12824 | 0.16051 | 0.16051 | 19.9703 |  | 0.38092 |  | 0.20737 | 1590 | 0.12824 |  | 0.16051
267 | 1596 | 0.11464 | 0.1584 | 0.1584 | 18.1579 |  | 0.36753 |  | 0.20599 | 1596 | 0.11464 |  | 0.1584
268 | 1602 | 0.10113 | 0.15629 | 0.15629 | 16.295 |  | 0.35401 |  | 0.20462 | 1602 | 0.10113 |  | 0.15629
269 | 1608 | 0.087717 | 0.15418 | 0.15418 | 14.3808 |  | 0.34033 |  | 0.20324 | 1608 | 0.087717 |  | 0.15418
270 | 1614 | 0.074414 | 0.15209 | 0.15209 | 12.4141 |  | 0.3265 |  | 0.20188 | 1614 | 0.074414 |  | 0.15209
271 | 1620 | 0.061224 | 0.15 | 0.15 | 10.3943 |  | 0.3125 |  | 0.20051 | 1620 | 0.061224 |  | 0.15
272 | 1626 | 0.048151 | 0.14792 | 0.14792 | 8.3203 |  | 0.29834 |  | 0.19916 | 1626 | 0.048151 |  | 0.14792
273 | 1632 | 0.035201 | 0.14586 | 0.14586 | 6.1917 |  | 0.28401 |  | 0.1978 | 1632 | 0.035201 |  | 0.14586
274 | 1638 | 0.022381 | 0.1438 | 0.1438 | 4.0075 |  | 0.26949 |  | 0.19646 | 1638 | 0.022381 |  | 0.1438
275 | 1644 | 0.0096948 | 0.14176 | 0.14176 | 1.7674 |  | 0.25479 |  | 0.19512 | 1644 | 0.0096948 |  | 0.14176
276 | 1650 | -0.0028502 | 0.13973 | 0.13973 | -0.52906 |  | 0.2399 |  | 0.19379 | 1650 | -0.0028502 |  | 0.13973
277 | 1656 | -0.015249 | 0.13772 | 0.13772 | -2.8823 |  | 0.2248 |  | 0.19247 | 1656 | -0.015249 |  | 0.13772
278 | 1662 | -0.027495 | 0.13573 | 0.13573 | -5.2924 |  | 0.20949 |  | 0.19115 | 1662 | -0.027495 |  | 0.13573
279 | 1668 | -0.039583 | 0.13376 | 0.13376 | -7.7593 |  | 0.19396 |  | 0.18985 | 1668 | -0.039583 |  | 0.13376
280 | 1674 | -0.051506 | 0.13181 | 0.13181 | -10.2828 |  | 0.17821 |  | 0.18855 | 1674 | -0.051506 |  | 0.13181
281 | 1680 | -0.06326 | 0.12989 | 0.12989 | -12.8625 |  | 0.16222 |  | 0.18727 | 1680 | -0.06326 |  | 0.12989
282 | 1686 | -0.074837 | 0.12799 | 0.12799 | -15.4977 |  | 0.14599 |  | 0.186 | 1686 | -0.074837 |  | 0.12799
283 | 1692 | -0.086232 | 0.12611 | 0.12611 | -18.1873 |  | 0.12951 |  | 0.18474 | 1692 | -0.086232 |  | 0.12611
284 | 1698 | -0.097439 | 0.12426 | 0.12426 | -20.9303 |  | 0.11276 |  | 0.18349 | 1698 | -0.097439 |  | 0.12426
285 | 1704 | -0.10845 | 0.12245 | 0.12245 | -23.7248 |  | 0.095743 |  | 0.18225 | 1704 | -0.10845 |  | 0.12245
286 | 1710 | -0.11926 | 0.12067 | 0.12067 | -26.569 |  | 0.078441 |  | 0.18103 | 1710 | -0.11926 |  | 0.12067
287 | 1716 | -0.12987 | 0.11891 | 0.11891 | -29.4605 |  | 0.060847 |  | 0.17983 | 1716 | -0.12987 |  | 0.11891
288 | 1722 | -0.14026 | 0.1172 | 0.1172 | -32.3965 |  | 0.042949 |  | 0.17863 | 1722 | -0.14026 |  | 0.1172
289 | 1728 | -0.15044 | 0.11552 | 0.11552 | -35.3736 |  | 0.024737 |  | 0.17745 | 1728 | -0.15044 |  | 0.11552
290 | 1734 | -0.16039 | 0.11389 | 0.11389 | -38.3881 |  | 0.0061981 |  | 0.17629 | 1734 | -0.16039 |  | 0.11389